## Voc & Isc Test Result
A1 Commissioning - IV Curve Testing | [10 empty] | Atterbury Boulevard
[11 empty] | Tested By: | Date:
I - V CURVE IN STRINGS | [6 empty] | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject |  |  | Cornelius Rheeders, Jaco Snyman | 2021-05-20
1 | Test carried out during a cloudless interval with irradiance above 600W/m2
2 | Test carried out before connecting the inverters to the loads
3 | Fuses removed prior to connection of the I-V tracer in the case that the PV Facility is connected to the electrical network
4 | Polarity of the strings measured and checked
5 | Measure and record the temperature measured on the backsheet of the PV module (Tm ) for thermographic camera or through the average of the temperature cell sensors
6 | Measure and record the Irradiance on the plane of the PV modules when performing the I-V curve
7 | Measure and record the open circuit voltage Voc across each string through the I-V tracer
8 | Measure and record the short circuit current (Isc ) of the string through the I-V tracer
Notes:
Only String 1 - 6 was tested by Cornelius and Jaco Snyman, the rest of the strings will be tested by Jaco and his team.
CALCULATIONS
Tc: temperature of the cell of the PV module will be calculated theoretically using the formula:
Tc | Temperature of the cell of the PV module (°C)
Tm | Temperature measured on the backsheet of the PV module (°C)
G | Irradiance on the plane of the PV modules (W/m2)
Gstc | Irradiance in STC (1000W/m2)
∆T | Temperature differences between PV cell and the PV backsheet, considered as 3 °C (as per IEC 61724, table A-1)
INVERTER 1 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 900 | 1000 | 45 |  | 3 | 47.7
| INPUT 2 |  | 703 | 1000 | 33 |  | 3 | 35.109
MPPT 2 | INPUT 1 |  | 703 | 1000 | 33 |  | 3 | 35.109
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 692 | 1000 | 36 |  | 3 | 38.076
| INPUT 2 |  | 695 | 1000 | 35 |  | 3 | 37.085
MPPT 4 | INPUT 1 |  | 698 | 1000 | 35 |  | 3 | 37.094
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 550 | 1000 | 34 |  | 3 | 35.65
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 550 | 1000 | 34 |  | 3 | 35.65
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 7 | INPUT 1 |  | 550 | 1000 | 34 |  | 3 | 35.65
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 8 | INPUT 1 |  | 552 | 1000 | 33 |  | 3 | 34.656
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 9 | INPUT 1 |  | 552 | 1000 | 36 |  | 3 | 37.656
| INPUT 2 |  | 552 | 1000 | 36 |  | 3 | 37.656
MPPT 10 | INPUT 1 |  | 713 | 1000 | 36 |  | 3 | 38.139
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 2 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 712 | 1000 | 30 |  | 3 | 32.136
| INPUT 2 |  | 712 | 1000 | 30 |  | 3 | 32.136
MPPT 2 | INPUT 1 |  | 712 | 1000 | 30 |  | 3 | 32.136
| INPUT 2 |  | 705 | 1000 | 32 |  | 3 | 34.115
MPPT 3 | INPUT 1 |  | 702 | 1000 | 32 |  | 3 | 34.106
| INPUT 2 |  | 702 | 1000 | 32 |  | 3 | 34.106
MPPT 4 | INPUT 1 |  | 702 | 1000 | 32 |  | 3 | 34.106
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 702 | 1000 | 0 |  | 3 | 2.106
| INPUT 2 |  | 702 | 1000 | 0 |  | 3 | 2.106
MPPT 6 | INPUT 1 |  | 702 | 1000 | 0 |  | 3 | 2.106
| INPUT 2 |  | 579 | 1000 | 30 |  | 3 | 31.737
MPPT 7 | INPUT 1 |  | 579 | 1000 | 30 |  | 3 | 31.737
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 8 | INPUT 1 |  | 579 | 1000 | 30 |  | 3 | 31.737
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 9 | INPUT 1 |  | 579 | 1000 | 30 |  | 3 | 31.737
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 10 | INPUT 1 |  | 579 | 1000 | 30 |  | 3 | 31.737
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 3 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 690 | 1000 | 30 |  | 3 | 32.07
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 611 | 1000 | 0 |  | 3 | 1.833
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 611 | 1000 | 0 |  | 3 | 1.833
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 611 | 1000 | 0 |  | 3 | 1.833
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 605 | 1000 | 33 |  | 3 | 34.815
| INPUT 2 |  | 605 | 1000 | 33 |  | 3 | 34.815
MPPT 6 | INPUT 1 |  | 605 | 1000 | 33 |  | 3 | 34.815
| INPUT 2 |  | 576 | 1000 | 29 |  | 3 | 30.728
MPPT 7 | INPUT 1 |  | 576 | 1000 | 29 |  | 3 | 30.728
| INPUT 2 |  | 576 | 1000 | 29 |  | 3 | 30.728
MPPT 8 | INPUT 1 |  | 576 | 1000 | 29 |  | 3 | 30.728
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 9 | INPUT 1 |  | 647 | 1000 | 35 |  | 3 | 36.941
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 10 | INPUT 1 |  | 647 | 1000 | 35 |  | 3 | 36.941
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 4 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 652 | 1000 | 32 |  | 3 | 33.956
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 652 | 1000 | 32 |  | 3 | 33.956
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 647 | 1000 | 35 |  | 3 | 36.941
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 647 | 1000 | 35 |  | 3 | 36.941
| INPUT 2 |  | 647 | 1000 | 35 |  | 3 | 36.941
MPPT 5 | INPUT 1 |  | 660 | 1000 | 35 |  | 3 | 36.98
| INPUT 2 |  | 660 | 1000 | 35 |  | 3 | 36.98
MPPT 6 | INPUT 1 |  | 662 | 1000 | 32 |  | 3 | 33.986
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 7 | INPUT 1 |  | 742 | 1000 | 31 |  | 3 | 33.226
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 8 | INPUT 1 |  | 688 | 1000 | 32 |  | 3 | 34.064
| INPUT 2 |  | 688 | 1000 | 32 |  | 3 | 34.064
MPPT 9 | INPUT 1 |  | 688 | 1000 | 32 |  | 3 | 34.064
| INPUT 2 |  | 688 | 1000 | 32 |  | 3 | 34.064
MPPT 10 | INPUT 1 |  | 688 | 1000 | 32 |  | 3 | 34.064
| INPUT 2 |  | 688 | 1000 | 32 |  | 3 | 34.064
INVERTER 5 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 703 | 1000 | 32 |  | 3 | 34.109
| INPUT 2 |  | 703 | 1000 | 32 |  | 3 | 34.109
MPPT 2 | INPUT 1 |  | 703 | 1000 | 32 |  | 3 | 34.109
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 792 | 1000 | 32 |  | 3 | 34.376
| INPUT 2 |  | 792 | 1000 | 32 |  | 3 | 34.376
MPPT 4 | INPUT 1 |  | 792 | 1000 | 32 |  | 3 | 34.376
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 753 | 1000 | 30 |  | 3 | 32.259
MPPT 6 | INPUT 1 |  | 753 | 1000 | 30 |  | 3 | 32.259
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 7 | INPUT 1 |  | 753 | 1000 | 30 |  | 3 | 32.259
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 8 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 764 | 1000 | 28 |  | 3 | 30.292
MPPT 9 | INPUT 1 |  | 764 | 1000 | 28 |  | 3 | 30.292
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 10 | INPUT 1 |  | 576 | 1000 | 29 |  | 3 | 30.728
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 6 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 576 | 1000 | 29 |  | 3 | 30.728
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 576 | 1000 | 29 |  | 3 | 30.728
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 718 | 1000 | 32 |  | 3 | 34.154
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 718 | 1000 | 32 |  | 3 | 34.154
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 718 | 1000 | 32 |  | 3 | 34.154
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 707 | 1000 | 41 |  | 3 | 43.121
| INPUT 2 |  | 707 | 1000 | 41 |  | 3 | 43.121
MPPT 7 | INPUT 1 |  | 718 | 1000 | 32 |  | 3 | 34.154
| INPUT 2 |  | 718 | 1000 | 32 |  | 3 | 34.154
MPPT 8 | INPUT 1 |  | 712 | 1000 | 30 |  | 3 | 32.136
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 9 | INPUT 1 |  | 576 | 1000 | 29 |  | 3 | 30.728
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 10 | INPUT 1 |  | 576 | 1000 | 29 |  | 3 | 30.728
| INPUT 2 |  | 576 | 1000 | 29 |  | 3 | 30.728
Voc theo : Theoretical open circuit voltage will be calculated theoretically using the formular:
Voc theo | Theoretical open circuit voltage (V)
Nmod | Number of the modules which compose each tested string
Voc stc | Rated PV module open circuit voltage at standard conditions (STC) (V)
δ Voc | PV module manufacturer's rated temperature coefficient of Voc (% / ° C)
Tc | Temperature of the cell of the PV module (°C)
INVERTER 1 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.93*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 14 | 51.91 | -0.23% |  | 47.7 | 688.7969 | 649 | 640.5811 | 94.22%
| INPUT 2 |  | 16 | 46.2 | -0.23% |  | 35.109 | 722.0131 | 735 | 671.4722 | 101.8%
MPPT 2 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 35.109 | 812.2647 | 834 | 755.4062 | 102.7%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 38.076 | 761.7793 | 776 | 708.4547 | 101.9%
| INPUT 2 |  | 17 | 46.2 | -0.23% |  | 37.085 | 763.5694 | 774 | 710.1196 | 101.4%
MPPT 4 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 37.094 | 763.5532 | 778 | 710.1044 | 101.9%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 5 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 35.65 | 766.1616 | 775 | 712.5303 | 101.2%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 6 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 35.65 | 766.1616 | 777 | 712.5303 | 101.4%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 7 | INPUT 1 |  | 19 | 46.2 | -0.23% |  | 35.65 | 856.2983 | 866 | 796.3574 | 101.1%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 8 | INPUT 1 |  | 19 | 46.2 | -0.23% |  | 34.656 | 858.3051 | 868 | 798.2238 | 101.1%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 9 | INPUT 1 |  | 16 | 46.2 | -0.23% |  | 37.656 | 717.6828 | 729 | 667.445 | 101.6%
| INPUT 2 |  | 16 | 46.2 | -0.23% |  | 37.656 | 717.6828 | 732 | 667.445 | 102%
MPPT 10 | INPUT 1 |  | 16 | 46.2 | -0.23% |  | 38.139 | 716.8616 | 736 | 666.6813 | 102.7%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
INVERTER 2 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.93*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 32.136 | 817.9511 | 818 | 760.6945 | 100%
| INPUT 2 |  | 18 | 46.2 | -0.23% |  | 32.136 | 817.9511 | 817 | 760.6945 | 99.88%
MPPT 2 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 32.136 | 817.9511 | 814 | 760.6945 | 99.52%
| INPUT 2 |  | 18 | 46.2 | -0.23% |  | 34.115 | 814.1659 | 822 | 757.1743 | 101%
MPPT 3 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 34.106 | 814.1831 | 822 | 757.1903 | 101%
| INPUT 2 |  | 18 | 46.2 | -0.23% |  | 34.106 | 814.1831 | 824 | 757.1903 | 101.2%
MPPT 4 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 34.106 | 814.1831 | 824 | 757.1903 | 101.2%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 5 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 2.106 | 826.7562 | 785 | 768.8832 | 94.95%
| INPUT 2 |  | 17 | 46.2 | -0.23% |  | 2.106 | 826.7562 | 777 | 768.8832 | 93.98%
MPPT 6 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 2.106 | 826.7562 | 0 | 768.8832 | 0%
| INPUT 2 |  | 17 | 46.2 | -0.23% |  | 31.737 | 773.2301 | 778 | 719.104 | 100.6%
MPPT 7 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 31.737 | 773.2301 | 774 | 719.104 | 100.1%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 8 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 31.737 | 773.2301 | 777 | 719.104 | 100.5%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 9 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 31.737 | 773.2301 | 775 | 719.104 | 100.2%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 10 | INPUT 1 |  | 19 | 46.2 | -0.23% |  | 31.737 | 864.1984 | 864 | 803.7045 | 99.98%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
INVERTER 3 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.93*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 20 | 46.2 | -0.23% |  | 32.07 | 908.9748 | 915 | 845.3466 | 100.7%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 2 | INPUT 1 |  | 20 | 46.2 | -0.23% |  | 1.833 | 973.2345 | 914 | 905.1081 | 93.91%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 |  | 20 | 46.2 | -0.23% |  | 1.833 | 973.2345 | 914 | 905.1081 | 93.91%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 4 | INPUT 1 |  | 20 | 46.2 | -0.23% |  | 1.833 | 973.2345 | 916 | 905.1081 | 94.12%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 5 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 34.815 | 812.827 | 821 | 755.9292 | 101%
| INPUT 2 |  | 18 | 46.2 | -0.23% |  | 34.815 | 812.827 | 0 | 755.9292 | 0%
MPPT 6 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 34.815 | 812.827 | 820 | 755.9292 | 100.9%
| INPUT 2 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 821 | 763.1991 | 100%
MPPT 7 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 814 | 763.1991 | 99.19%
| INPUT 2 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 810 | 763.1991 | 98.7%
MPPT 8 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 816 | 763.1991 | 99.43%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 9 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 36.941 | 808.7607 | 812 | 752.1474 | 100.4%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 10 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 36.941 | 808.7607 | 815 | 752.1474 | 100.8%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
INVERTER 4 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.93*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 33.956 | 769.2217 | 788 | 715.3762 | 102.4%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 2 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 33.956 | 769.2217 | 781 | 715.3762 | 101.5%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 |  | 16 | 46.2 | -0.23% |  | 36.941 | 718.8984 | 731 | 668.5755 | 101.7%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 4 | INPUT 1 |  | 16 | 46.2 | -0.23% |  | 36.941 | 718.8984 | 730 | 668.5755 | 101.5%
| INPUT 2 |  | 16 | 46.2 | -0.23% |  | 36.941 | 718.8984 | 730 | 668.5755 | 101.5%
MPPT 5 | INPUT 1 |  | 16 | 46.2 | -0.23% |  | 36.98 | 718.8321 | 731 | 668.5138 | 101.7%
| INPUT 2 |  | 16 | 46.2 | -0.23% |  | 36.98 | 718.8321 | 729 | 668.5138 | 101.4%
MPPT 6 | INPUT 1 |  | 16 | 46.2 | -0.23% |  | 33.986 | 723.9224 | 729 | 673.2478 | 100.7%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 7 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 33.226 | 770.5404 | 0 | 716.6026 | 0%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 8 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 34.064 | 769.0266 | 770 | 715.1947 | 100.1%
| INPUT 2 |  | 17 | 46.2 | -0.23% |  | 34.064 | 769.0266 | 767 | 715.1947 | 99.74%
MPPT 9 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 34.064 | 769.0266 | 767 | 715.1947 | 99.74%
| INPUT 2 |  | 17 | 46.2 | -0.23% |  | 34.064 | 769.0266 | 766 | 715.1947 | 99.61%
MPPT 10 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 34.064 | 769.0266 | 768 | 715.1947 | 99.87%
| INPUT 2 |  | 17 | 46.2 | -0.23% |  | 34.064 | 769.0266 | 772 | 715.1947 | 100.4%
INVERTER 5 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.93*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 34.109 | 814.1774 | 828 | 757.185 | 101.7%
| INPUT 2 |  | 18 | 46.2 | -0.23% |  | 34.109 | 814.1774 | 0 | 757.185 | 0%
MPPT 2 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 34.109 | 814.1774 | 823 | 757.185 | 101.1%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 |  | 16 | 46.2 | -0.23% |  | 34.376 | 723.2593 | 720 | 672.6311 | 99.55%
| INPUT 2 |  | 16 | 46.2 | -0.23% |  | 34.376 | 723.2593 | 721 | 672.6311 | 99.69%
MPPT 4 | INPUT 1 |  | 16 | 46.2 | -0.23% |  | 34.376 | 723.2593 | 717 | 672.6311 | 99.13%
| INPUT 2 |  | 16 | 46.2 | -0.23% |  | 0 | 781.704 | 719 | 726.9847 | 91.98%
MPPT 5 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 0 | 830.5605 | 774 | 772.4213 | 93.19%
| INPUT 2 |  | 17 | 46.2 | -0.23% |  | 32.259 | 772.2872 | 776 | 718.2271 | 100.5%
MPPT 6 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 32.259 | 772.2872 | 781 | 718.2271 | 101.1%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 7 | INPUT 1 |  | 16 | 46.2 | -0.23% |  | 32.259 | 726.8585 | 724 | 675.9784 | 99.61%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 8 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 0 | 879.417 | 0 | 817.8578 | 0%
| INPUT 2 |  | 18 | 46.2 | -0.23% |  | 30.292 | 821.4781 | 818 | 763.9746 | 99.58%
MPPT 9 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 30.292 | 775.8404 | 761 | 721.5316 | 98.09%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 10 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 822 | 763.1991 | 100.2%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
INVERTER 6 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.93*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 822 | 763.1991 | 100.2%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 2 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 821 | 763.1991 | 100%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 |  | 19 | 46.2 | -0.23% |  | 34.154 | 859.3186 | 822 | 799.1663 | 95.66%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 4 | INPUT 1 |  | 19 | 46.2 | -0.23% |  | 34.154 | 859.3186 | 849 | 799.1663 | 98.8%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 5 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 34.154 | 814.0913 | 809 | 757.1049 | 99.37%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 6 | INPUT 1 |  | 19 | 46.2 | -0.23% |  | 43.121 | 841.2148 | 849 | 782.3298 | 100.9%
| INPUT 2 |  | 19 | 46.2 | -0.23% |  | 43.121 | 841.2148 | 850 | 782.3298 | 101%
MPPT 7 | INPUT 1 |  | 19 | 46.2 | -0.23% |  | 34.154 | 859.3186 | 0 | 799.1663 | 0%
| INPUT 2 |  | 19 | 46.2 | -0.23% |  | 34.154 | 859.3186 | 863 | 799.1663 | 100.4%
MPPT 8 | INPUT 1 |  | 17 | 46.2 | -0.23% |  | 32.136 | 772.5094 | 776 | 718.4337 | 100.5%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 9 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 813 | 763.1991 | 99.07%
| INPUT 2 |  | 0 | 46.2 | -0.23% |  | 0 | 0 | 0 | 0
MPPT 10 | INPUT 1 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 829 | 763.1991 | 101%
| INPUT 2 |  | 18 | 46.2 | -0.23% |  | 30.728 | 820.6442 | 0 | 763.1991 | 0%
Isc theo : Theoretical short circuit current will be calculated theoretically using the formula:
N | Number of strings which compose each test
Isc stc | Rated PV module short circuit curent at standard conditions indicated in the photovoltaic panel data sheet (STC) (A)
G | Irradiance on the plane of the PV modules (W/m2)
Gstc | Irradiance in STC conditions (1000 W/m2)
δIsc | PV module manufacturer's rated temperature coefficient of Isc (% / °C)
Tc | Temperature of the cell of the PV module (°C)
Isc theo | Theoretical short circuit current (A)
INVERTER 1 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.90*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 14.07 | 900 | 1000 | 0.05% | 47.7 | 12.8067 | 5.45 | 11.9103 | 42.56%
| INPUT 2 | 1 | 14.07 | 703 | 1000 | 0.05% | 35.109 | 9.9412 | 5.94 | 9.2453 | 59.75%
MPPT 2 | INPUT 1 | 1 | 14.07 | 703 | 1000 | 0.05% | 35.109 | 9.9412 | 6.48 | 9.2453 | 65.18%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 | 1 | 14.07 | 692 | 1000 | 0.05% | 38.076 | 9.8001 | 7.62 | 9.1141 | 77.75%
| INPUT 2 | 1 | 14.07 | 695 | 1000 | 0.05% | 37.085 | 9.8377 | 7.68 | 9.1491 | 78.07%
MPPT 4 | INPUT 1 | 1 | 14.07 | 698 | 1000 | 0.05% | 37.094 | 9.8802 | 7.64 | 9.1886 | 77.33%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 5 | INPUT 1 | 1 | 14.07 | 550 | 1000 | 0.05% | 35.65 | 7.7797 | 7.58 | 7.2351 | 97.43%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 6 | INPUT 1 | 1 | 14.07 | 550 | 1000 | 0.05% | 35.65 | 7.7797 | 7.57 | 7.2351 | 97.3%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 7 | INPUT 1 | 1 | 14.07 | 550 | 1000 | 0.05% | 35.65 | 7.7797 | 7.63 | 7.2351 | 98.08%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 8 | INPUT 1 | 1 | 14.07 | 552 | 1000 | 0.05% | 34.656 | 7.8041 | 7.61 | 7.2578 | 97.51%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 9 | INPUT 1 | 1 | 14.07 | 552 | 1000 | 0.05% | 37.656 | 7.8158 | 7.65 | 7.2687 | 97.88%
| INPUT 2 | 1 | 14.07 | 552 | 1000 | 0.05% | 37.656 | 7.8158 | 7.59 | 7.2687 | 97.11%
MPPT 10 | INPUT 1 | 1 | 14.07 | 713 | 1000 | 0.05% | 38.139 | 10.0978 | 7.55 | 9.391 | 74.77%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
INVERTER 2 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.90*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 14.07 | 712 | 1000 | 0.05% | 32.136 | 10.0536 | 6.17 | 9.3498 | 61.37%
| INPUT 2 | 1 | 14.07 | 712 | 1000 | 0.05% | 32.136 | 10.0536 | 6.1 | 9.3498 | 60.67%
MPPT 2 | INPUT 1 | 1 | 14.07 | 712 | 1000 | 0.05% | 32.136 | 10.0536 | 6.14 | 9.3498 | 61.07%
| INPUT 2 | 1 | 14.07 | 705 | 1000 | 0.05% | 34.115 | 9.9646 | 6.11 | 9.267 | 61.32%
MPPT 3 | INPUT 1 | 1 | 14.07 | 702 | 1000 | 0.05% | 34.106 | 9.9221 | 6.32 | 9.2276 | 63.7%
| INPUT 2 | 1 | 14.07 | 702 | 1000 | 0.05% | 34.106 | 9.9221 | #REF! | 9.2276
MPPT 4 | INPUT 1 | 1 | 14.07 | 702 | 1000 | 0.05% | 34.106 | 9.9221 | 6.17 | 9.2276 | 62.18%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 5 | INPUT 1 | 1 | 14.07 | 702 | 1000 | 0.05% | 2.106 | 9.7641 | 7.45 | 9.0806 | 76.3%
| INPUT 2 | 1 | 14.07 | 702 | 1000 | 0.05% | 2.106 | 9.7641 | 7.49 | 9.0806 | 76.71% |  | 702 | 7.49
MPPT 6 | INPUT 1 | 1 | 14.07 | 702 | 1000 | 0.05% | 2.106 | 9.7641 | 0 | 9.0806 | 0%
| INPUT 2 | 1 | 14.07 | 579 | 1000 | 0.05% | 31.737 | 8.174 | 7.39 | 7.6018 | 90.41%
MPPT 7 | INPUT 1 | 1 | 14.07 | 579 | 1000 | 0.05% | 31.737 | 8.174 | 7.35 | 7.6018 | 89.92%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 8 | INPUT 1 | 1 | 14.07 | 579 | 1000 | 0.05% | 31.737 | 8.174 | 7.27 | 7.6018 | 88.94%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 9 | INPUT 1 | 1 | 14.07 | 579 | 1000 | 0.05% | 31.737 | 8.174 | 7.29 | 7.6018 | 89.19%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 10 | INPUT 1 | 1 | 14.07 | 579 | 1000 | 0.05% | 31.737 | 8.174 | 7.23 | 7.6018 | 88.45%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
INVERTER 3 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.90*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 14.07 | 690 | 1000 | 0.05% | 32.07 | 9.7426 | 5.77 | 9.0606 | 59.22%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 2 | INPUT 1 | 1 | 14.07 | 611 | 1000 | 0.05% | 1.833 | 8.4972 | 5.77 | 7.9024 | 67.9%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 | 1 | 14.07 | 611 | 1000 | 0.05% | 1.833 | 8.4972 | 5.72 | 7.9024 | 67.32%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 4 | INPUT 1 | 1 | 14.07 | 611 | 1000 | 0.05% | 1.833 | 8.4972 | 5.66 | 7.9024 | 66.61%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 5 | INPUT 1 | 1 | 14.07 | 605 | 1000 | 0.05% | 34.815 | 8.5541 | 7.17 | 7.9553 | 83.82% |  | 605 | 7.17
| INPUT 2 | 1 | 14.07 | 605 | 1000 | 0.05% | 34.815 | 8.5541 | 0 | 7.9553 | 0%
MPPT 6 | INPUT 1 | 1 | 14.07 | 605 | 1000 | 0.05% | 34.815 | 8.5541 | 7.14 | 7.9553 | 83.47% |  | 605 | 7.14
| INPUT 2 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 7.04 | 7.5586 | 86.62% |  | 576 | 7.04
MPPT 7 | INPUT 1 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 7 | 7.5586 | 86.13%
| INPUT 2 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 7.07 | 7.5586 | 86.99%
MPPT 8 | INPUT 1 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 6.96 | 7.5586 | 85.63%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 9 | INPUT 1 | 1 | 14.07 | 647 | 1000 | 0.05% | 36.941 | 9.1576 | 7 | 8.5166 | 76.44%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 10 | INPUT 1 | 1 | 14.07 | 647 | 1000 | 0.05% | 36.941 | 9.1576 | 6.98 | 8.5166 | 76.22%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
INVERTER 4 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.90*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 14.07 | 652 | 1000 | 0.05% | 33.956 | 9.2147 | 6.26 | 8.5697 | 67.93%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 2 | INPUT 1 | 1 | 14.07 | 652 | 1000 | 0.05% | 33.956 | 9.2147 | 6.39 | 8.5697 | 69.35%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 | 1 | 14.07 | 647 | 1000 | 0.05% | 36.941 | 9.1576 | 6.07 | 8.5166 | 66.28%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 4 | INPUT 1 | 1 | 14.07 | 647 | 1000 | 0.05% | 36.941 | 9.1576 | 6.05 | 8.5166 | 66.07%
| INPUT 2 | 1 | 14.07 | 647 | 1000 | 0.05% | 36.941 | 9.1576 | 5.82 | 8.5166 | 63.55%
MPPT 5 | INPUT 1 | 1 | 14.07 | 660 | 1000 | 0.05% | 36.98 | 9.3418 | 5.93 | 8.6879 | 63.48%
| INPUT 2 | 1 | 14.07 | 660 | 1000 | 0.05% | 36.98 | 9.3418 | 5.41 | 8.6879 | 57.91%
MPPT 6 | INPUT 1 | 1 | 14.07 | 662 | 1000 | 0.05% | 33.986 | 9.3562 | 7.18 | 8.7013 | 76.74%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 7 | INPUT 1 | 1 | 14.07 | 742 | 1000 | 0.05% | 33.226 | 10.4829 | 0 | 9.7491 | 0%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 8 | INPUT 1 | 1 | 14.07 | 688 | 1000 | 0.05% | 34.064 | 9.724 | 8.7 | 9.0433 | 89.47%
| INPUT 2 | 1 | 14.07 | 688 | 1000 | 0.05% | 34.064 | 9.724 | 9.38 | 9.0433 | 96.46%
MPPT 9 | INPUT 1 | 1 | 14.07 | 688 | 1000 | 0.05% | 34.064 | 9.724 | 9.27 | 9.0433 | 95.33%
| INPUT 2 | 1 | 14.07 | 688 | 1000 | 0.05% | 34.064 | 9.724 | 9.23 | 9.0433 | 94.92%
MPPT 10 | INPUT 1 | 1 | 14.07 | 688 | 1000 | 0.05% | 34.064 | 9.724 | 9.19 | 9.0433 | 94.51%
| INPUT 2 | 1 | 14.07 | 688 | 1000 | 0.05% | 34.064 | 9.724 | 8.16 | 9.0433 | 83.92%
INVERTER 5 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.90*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 14.07 | 703 | 1000 | 0.05% | 34.109 | 9.9363 | 5.84 | 9.2407 | 58.77%
| INPUT 2 | 1 | 14.07 | 703 | 1000 | 0.05% | 34.109 | 9.9363 | 0 | 9.2407 | 0%
MPPT 2 | INPUT 1 | 1 | 14.07 | 703 | 1000 | 0.05% | 34.109 | 9.9363 | 5.87 | 9.2407 | 59.08%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 | 1 | 14.07 | 792 | 1000 | 0.05% | 34.376 | 11.1957 | 8.92 | 10.412 | 79.67%
| INPUT 2 | 1 | 14.07 | 792 | 1000 | 0.05% | 34.376 | 11.1957 | 9.02 | 10.412 | 80.57%
MPPT 4 | INPUT 1 | 1 | 14.07 | 792 | 1000 | 0.05% | 34.376 | 11.1957 | 8.59 | 10.412 | 76.73%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 8.64 | 0
MPPT 5 | INPUT 1 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 7.87 | 0
| INPUT 2 | 1 | 14.07 | 753 | 1000 | 0.05% | 32.259 | 10.6332 | 7.87 | 9.8888 | 74.01%
MPPT 6 | INPUT 1 | 1 | 14.07 | 753 | 1000 | 0.05% | 32.259 | 10.6332 | 8.15 | 9.8888 | 76.65%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 7 | INPUT 1 | 1 | 14.07 | 753 | 1000 | 0.05% | 32.259 | 10.6332 | 8.67 | 9.8888 | 81.54% |  | 753 | 8.67
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 8 | INPUT 1 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
| INPUT 2 | 1 | 14.07 | 764 | 1000 | 0.05% | 30.292 | 10.7779 | 10.27 | 10.0235 | 95.29%
MPPT 9 | INPUT 1 | 1 | 14.07 | 764 | 1000 | 0.05% | 30.292 | 10.7779 | 8.06 | 10.0235 | 74.78%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 10 | INPUT 1 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 9 | 7.5586 | 110.7%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
INVERTER 6 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.90*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 6.45 | 7.5586 | 79.36%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 2 | INPUT 1 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 6.43 | 7.5586 | 79.11%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 3 | INPUT 1 | 1 | 14.07 | 718 | 1000 | 0.05% | 34.154 | 10.1485 | 6.1 | 9.4381 | 60.11%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 4 | INPUT 1 | 1 | 14.07 | 718 | 1000 | 0.05% | 34.154 | 10.1485 | 7.31 | 9.4381 | 72.03%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 5 | INPUT 1 | 1 | 14.07 | 718 | 1000 | 0.05% | 34.154 | 10.1485 | 7.36 | 9.4381 | 72.52%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 6 | INPUT 1 | 1 | 14.07 | 707 | 1000 | 0.05% | 43.121 | 10.0376 | 7.37 | 9.335 | 73.42%
| INPUT 2 | 1 | 14.07 | 707 | 1000 | 0.05% | 43.121 | 10.0376 | 7.42 | 9.335 | 73.92%
MPPT 7 | INPUT 1 | 1 | 14.07 | 718 | 1000 | 0.05% | 34.154 | 10.1485 | 0 | 9.4381 | 0%
| INPUT 2 | 1 | 14.07 | 718 | 1000 | 0.05% | 34.154 | 10.1485 | 7.61 | 9.4381 | 74.99%
MPPT 8 | INPUT 1 | 1 | 14.07 | 712 | 1000 | 0.05% | 32.136 | 10.0536 | 6.28 | 9.3498 | 62.47%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 9 | INPUT 1 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 6.25 | 7.5586 | 76.9%
| INPUT 2 | 1 | 14.07 | 0 | 1000 | 0.05% | 0 | 0 | 0 | 0
MPPT 10 | INPUT 1 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 6.31 | 7.5586 | 77.64%
| INPUT 2 | 1 | 14.07 | 576 | 1000 | 0.05% | 30.728 | 8.1275 | 0 | 7.5586 | 0%
No string may have a measured Voc that differs by less than 10% from the theoretical (Voc > 0.9* Voc theo).
No string may have a measured Isc that differs by less than 10% from the theoretical (Isc > 0.9 * Isc theo).
Strings polarity must be correct.
The accuracy of the I-V tracer and the infrared camera used will be considered.

## Raw Data_Mod Tests
Inverter | MPPT | String | Tc | G | Tm | Voc Measure | Isc Measure | Voc stc Check | Column1 | N | Gstc | ΔT | Voc theo | Nmod | Voc stc | Ic | δ Voc | Tc | Isc stc | δIsc | Isc theo | Tc | Temperature of the cell of the PV module (°C)
1 | 1 | 1 | 47.7 | 900 | 45 | 649 | 5.45 |  |  | 14 | 1000 | 3 |  | 14 | 94.22% | 42.56% | -0.23% |  | 14.07 | 0.05% |  | Tm | Temperature measured on the backsheet of the PV module (°C)
|  | 2 | 35.109 | 703 | 33 | 735 | 5.94 |  |  | 16 | 1000 | 3 |  | 16 | 101.8% | 59.75% | [5 empty] | G | Irradiance on the plane of the PV modules (W/m2)
| 2 | 3 | 35.109 | 703 | 33 | 834 | 6.48 |  |  | 18 | 1000 | 3 |  | 18 | 102.7% | 65.18% | [5 empty] | Gstc | Irradiance in STC (1000W/m2)
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0 | [7 empty] | ∆T | Temperature differences between PV cell and the PV backsheet, considered as 3 °C (as per IEC 61724, table A-1)
| 3 | 4 | 38.076 | 692 | 36 | 776 | 7.62 |  |  | 17 | 1000 | 3 |  | 17 | 101.9% | 77.75% | [5 empty] | Voc theo | Theoratical open circuit voltage (V)
|  | 5 | 37.085 | 695 | 35 | 774 | 7.68 |  |  | 17 | 1000 | 3 |  | 17 | 101.4% | 78.07% | [5 empty] | Nmod | Number of the modules which compose each tested string
| 4 | 6 | 37.094 | 698 | 35 | 778 | 7.64 |  |  | 17 | 1000 | 3 |  | 17 | 101.9% | 77.33% | [5 empty] | Voc stc | Rated PV module open circuit voltage at standard conditions (STC) (V)
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0 | [7 empty] | δ Voc | PV module manufacturer's rated temperature coefficient of Voc (% / ° C)
| 5 | 7 | 35.65 | 550 | 34 | 775 | 7.58 |  |  | 17 | 1000 | 3 |  | 17 | 101.2% | 97.43% | [5 empty] | Tc | Temperature of the cell of the PV module (°C)
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0 | [7 empty] | N | Number of strings which compose each test
| 6 | 8 | 35.65 | 550 | 34 | 777 | 7.57 |  |  | 17 | 1000 | 3 |  | 17 | 101.4% | 97.3% | [5 empty] | Isc stc | Rated PV module short circuit curent at standard conditions indicated in the photovoltaic panel data sheet (STC) (A)
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0 | [7 empty] | G | Irradiance on the plane of the PV modules (W/m2)
| 7 | 9 | 35.65 | 550 | 34 | 866 | 7.63 |  |  | 19 | 1000 | 3 |  | 19 | 101.1% | 98.08%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 8 | 10 | 34.656 | 552 | 33 | 868 | 7.61 |  |  | 19 | 1000 | 3 |  | 19 | 101.1% | 97.51%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 9 | 11 | 37.656 | 552 | 36 | 729 | 7.65 |  |  | 16 | 1000 | 3 |  | 16 | 101.6% | 97.88%
|  | 12 | 37.656 | 552 | 36 | 732 | 7.59 |  |  | 16 | 1000 | 3 |  | 16 | 102% | 97.11%
| 10 | 13 | 38.139 | 713 | 36 | 736 | 7.55 |  |  | 16 | 1000 | 3 |  | 16 | 102.7% | 74.77%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
2 | 1 | 14 | 32.136 | 712 | 30 | 818 | 6.17 |  |  | 18 | 1000 | 3 |  | 18 | 100% | 61.37% | [5 empty] | Gstc | Irradiance in STC conditions (1000 W/m2)
|  | 15 | 32.136 | 712 | 30 | 817 | 6.1 |  |  | 18 | 1000 | 3 |  | 18 | 99.88% | 60.67% | [5 empty] | δIsc | PV module manufacturer's rated temperature coefficient of Isc (% / °C)
| 2 | 16 | 32.136 | 712 | 30 | 814 | 6.14 |  |  | 18 | 1000 | 3 |  | 18 | 99.52% | 61.07% | [5 empty] | Tc | Temperature of the cell of the PV module (°C)
|  | 17 | 34.115 | 705 | 32 | 822 | 6.11 |  |  | 18 | 1000 | 3 |  | 18 | 101% | 61.32% | [5 empty] | Isc theo | Theoratical short circuit current (A)
| 3 | 18 | 34.106 | 702 | 32 | 822 | 6.32 |  |  | 18 | 1000 | 3 |  | 18 | 101% | 63.7%
|  | 19 | 34.106 | 702 | 32 | 824 | 6.42 |  |  | 18 | 1000 | 3 |  | 18 | 101.2%
| 4 | 20 | 34.106 | 702 | 32 | 824 | 6.17 |  |  | 18 | 1000 | 3 |  | 18 | 101.2% | 62.18%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 5 | 21 | 2.106 | 702 |  | 785 | 7.45 |  |  | 17 | 1000 | 3 |  | 17 | 94.95% | 76.3%
|  | 22 | 2.106 | 702 |  | 777 | 7.49 |  |  | 17 | 1000 | 3 |  | 17 | 93.98% | 76.71%
| 6 | 23 | 2.106 | 702 | [5 empty] | 17 | 1000 | 3 |  | 17 | 0% | 0%
|  | 24 | 31.737 | 579 | 30 | 778 | 7.39 |  |  | 17 | 1000 | 3 |  | 17 | 100.6% | 90.41%
| 7 | 25 | 31.737 | 579 | 30 | 774 | 7.35 |  |  | 17 | 1000 | 3 |  | 17 | 100.1% | 89.92%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 8 | 26 | 31.737 | 579 | 30 | 777 | 7.27 |  |  | 17 | 1000 | 3 |  | 17 | 100.5% | 88.94%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 9 | 27 | 31.737 | 579 | 30 | 775 | 7.29 |  |  | 17 | 1000 | 3 |  | 17 | 100.2% | 89.19%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 10 | 28 | 31.737 | 579 | 30 | 864 | 7.23 |  |  | 19 | 1000 | 3 |  | 19 | 99.98% | 88.45%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
3 | 1 | 29 | 32.07 | 690 | 30 | 915 | 5.77 |  |  | 20 | 1000 | 3 |  | 20 | 100.7% | 59.22%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 2 | 30 | 1.833 | 611 |  | 914 | 5.77 |  |  | 20 | 1000 | 3 |  | 20 | 93.91% | 67.9%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 3 | 31 | 1.833 | 611 |  | 914 | 5.72 |  |  | 20 | 1000 | 3 |  | 20 | 93.91% | 67.32%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 4 | 32 | 1.833 | 611 |  | 916 | 5.66 |  |  | 20 | 1000 | 3 |  | 20 | 94.12% | 66.61%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 5 | 33 | 34.815 | 605 | 33 | 821 | 7.17 |  |  | 18 | 1000 | 3 |  | 18 | 101% | 83.82%
|  | 34 | 34.815 | 605 | 33 |  |  |  |  | 18 | 1000 | 3 |  | 18 | 0% | 0%
| 6 | 35 | 34.815 | 605 | 33 | 820 | 7.14 |  |  | 18 | 1000 | 3 |  | 18 | 100.9% | 83.47%
|  | 36 | 30.728 | 576 | 29 | 821 | 7.04 |  |  | 18 | 1000 | 3 |  | 18 | 100% | 86.62%
| 7 | 37 | 30.728 | 576 | 29 | 814 | 7 |  |  | 18 | 1000 | 3 |  | 18 | 99.19% | 86.13%
|  | 38 | 30.728 | 576 | 29 | 810 | 7.07 |  |  | 18 | 1000 | 3 |  | 18 | 98.7% | 86.99%
| 8 | 39 | 30.728 | 576 | 29 | 816 | 6.96 |  |  | 18 | 1000 | 3 |  | 18 | 99.43% | 85.63%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 9 | 40 | 36.941 | 647 | 35 | 812 | 7 |  |  | 18 | 1000 | 3 |  | 18 | 100.4% | 76.44%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 10 | 41 | 36.941 | 647 | 35 | 815 | 6.98 |  |  | 18 | 1000 | 3 |  | 18 | 100.8% | 76.22%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
4 | 1 | 42 | 33.956 | 652 | 32 | 788 | 6.26 |  |  | 17 | 1000 | 3 |  | 17 | 102.4% | 67.93%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 2 | 43 | 33.956 | 652 | 32 | 781 | 6.39 |  |  | 17 | 1000 | 3 |  | 17 | 101.5% | 69.35%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 3 | 44 | 36.941 | 647 | 35 | 731 | 6.07 |  |  | 16 | 1000 | 3 |  | 16 | 101.7% | 66.28%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 4 | 45 | 36.941 | 647 | 35 | 730 | 6.05 |  |  | 16 | 1000 | 3 |  | 16 | 101.5% | 66.07%
|  | 46 | 36.941 | 647 | 35 | 730 | 5.82 |  |  | 16 | 1000 | 3 |  | 16 | 101.5% | 63.55%
| 5 | 47 | 36.98 | 660 | 35 | 731 | 5.93 |  |  | 16 | 1000 | 3 |  | 16 | 101.7% | 63.48%
|  | 48 | 36.98 | 660 | 35 | 729 | 5.41 |  |  | 16 | 1000 | 3 |  | 16 | 101.4% | 57.91%
| 6 | 49 | 33.986 | 662 | 32 | 729 | 7.18 |  |  | 16 | 1000 | 3 |  | 16 | 100.7% | 76.74%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 7 | 50 | 33.226 | 742 | 31 |  |  |  |  | 17 | 1000 | 3 |  | 17 | 0% | 0%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 8 | 51 | 34.064 | 688 | 32 | 770 | 8.7 |  |  | 17 | 1000 | 3 |  | 17 | 100.1% | 89.47%
|  | 52 | 34.064 | 688 | 32 | 767 | 9.38 |  |  | 17 | 1000 | 3 |  | 17 | 99.74% | 96.46%
| 9 | 53 | 34.064 | 688 | 32 | 767 | 9.27 |  |  | 17 | 1000 | 3 |  | 17 | 99.74% | 95.33%
|  | 54 | 34.064 | 688 | 32 | 766 | 9.23 |  |  | 17 | 1000 | 3 |  | 17 | 99.61% | 94.92%
| 10 | 55 | 34.064 | 688 | 32 | 768 | 9.19 |  |  | 17 | 1000 | 3 |  | 17 | 99.87% | 94.51%
|  | 56 | 34.064 | 688 | 32 | 772 | 8.16 |  |  | 17 | 1000 | 3 |  | 17 | 100.4% | 83.92%
5 | 1 | 57 | 34.109 | 703 | 32 | 828 | 5.84 |  |  | 18 | 1000 | 3 |  | 18 | 101.7% | 58.77%
|  | 58 | 34.109 | 703 | 32 |  |  |  |  | 18 | 1000 | 3 |  | 18 | 0% | 0%
| 2 | 59 | 34.109 | 703 | 32 | 823 | 5.87 |  |  | 18 | 1000 | 3 |  | 18 | 101.1% | 59.08%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 3 | 60 | 34.376 | 792 | 32 | 720 | 8.92 |  |  | 16 | 1000 | 3 |  | 16 | 99.55% | 79.67%
|  | 61 | 34.376 | 792 | 32 | 721 | 9.02 |  |  | 16 | 1000 | 3 |  | 16 | 99.69% | 80.57%
| 4 | 62 | 34.376 | 792 | 32 | 717 | 8.59 |  |  | 16 | 1000 | 3 |  | 16 | 99.13% | 76.73%
|  | 63 | 0 |  |  | 719 | 8.64 |  |  | 16 | 1000 | 3 |  | 16 | 91.98%
| 5 | 64 | 0 |  |  | 774 | 7.87 |  |  | 17 | 1000 | 3 |  | 17 | 93.19%
|  | 65 | 32.259 | 753 | 30 | 776 | 7.87 |  |  | 17 | 1000 | 3 |  | 17 | 100.5% | 74.01%
| 6 | 66 | 32.259 | 753 | 30 | 781 | 8.15 |  |  | 17 | 1000 | 3 |  | 17 | 101.1% | 76.65%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 7 | 67 | 32.259 | 753 | 30 | 724 | 8.67 |  |  | 16 | 1000 | 3 |  | 16 | 99.61% | 81.54%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 8 | 68 | 0 | [6 empty] | 18 | 1000 | 3 |  | 18 | 0%
|  | 69 | 30.292 | 764 | 28 | 818 | 10.27 |  |  | 18 | 1000 | 3 |  | 18 | 99.58% | 95.29%
| 9 | 70 | 30.292 | 764 | 28 | 761 | 8.06 |  |  | 17 | 1000 | 3 |  | 17 | 98.09% | 74.78%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 10 | 71 | 30.728 | 576 | 29 | 822 | 9 |  |  | 18 | 1000 | 3 |  | 18 | 100.2% | 110.7%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
6 | 1 | 72 | 30.728 | 576 | 29 | 822 | 6.45 |  |  | 18 | 1000 | 3 |  | 18 | 100.2% | 79.36%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 2 | 73 | 30.728 | 576 | 29 | 821 | 6.43 |  |  | 18 | 1000 | 3 |  | 18 | 100% | 79.11%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 3 | 74 | 34.154 | 718 | 32 | 822 | 6.1 |  |  | 19 | 1000 | 3 |  | 19 | 95.66% | 60.11%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 4 | 75 | 34.154 | 718 | 32 | 849 | 7.31 |  |  | 19 | 1000 | 3 |  | 19 | 98.8% | 72.03%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 5 | 76 | 34.154 | 718 | 32 | 809 | 7.36 |  |  | 18 | 1000 | 3 |  | 18 | 99.37% | 72.52%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 6 | 77 | 43.121 | 707 | 41 | 849 | 7.37 |  |  | 19 | 1000 | 3 |  | 19 | 100.9% | 73.42%
|  | 78 | 43.121 | 707 | 41 | 850 | 7.42 |  |  | 19 | 1000 | 3 |  | 19 | 101% | 73.92%
| 7 | 79 | 34.154 | 718 | 32 |  |  |  |  | 19 | 1000 | 3 |  | 19 | 0% | 0%
|  | 80 | 34.154 | 718 | 32 | 863 | 7.61 |  |  | 19 | 1000 | 3 |  | 19 | 100.4% | 74.99%
| 8 | 81 | 32.136 | 712 | 30 | 776 | 6.28 |  |  | 17 | 1000 | 3 |  | 17 | 100.5% | 62.47%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 9 | 82 | 30.728 | 576 | 29 | 813 | 6.25 |  |  | 18 | 1000 | 3 |  | 18 | 99.07% | 76.9%
|  |  | #DIV/0! | [7 empty] | 0 | 0 |  | 0
| 10 | 83 | 30.728 | 576 | 29 | 829 | 6.31 |  |  | 18 | 1000 | 3 |  | 18 | 101% | 77.64%
|  | 84 | 30.728 | 576 | 29 |  |  |  |  | 18 | 1000 | 3 |  | 18 | 0% | 0%
Isc theo
Isc theo
Isc theo
Isc theo
Note on K1: Dayne Sage: Number of modules in Series

## Sheet4
Inverter | MPPT | String | Tc | G | Tm
1 | 1 | 1 | 47.7 | 703 | 33
|  | 2 | 35.109 | 703 | 33
| 2 | 3 | 35.109 | 703 | 33
| 3 | 4 | 38.076 | 692 | 36
|  | 5 | 37.085 | 695 | 35
| 4 | 6 | 37.094 | 698 | 35
| 5 | 7 | 35.65 | 550 | 34
| 6 | 8 | 35.65 | 550 | 34
| 7 | 9 | 35.65 | 550 | 34
| 8 | 10 | 34.656 | 552 | 33
| 9 | 11 | 37.656 | 552 | 36
|  | 12 | 37.656 | 552 | 36
| 10 | 13 | 38.139 | 713 | 36
2 | 1 | 14 | 32.136 | 712 | 30
|  | 15 | 32.136 | 712 | 30
| 2 | 16 | 32.136 | 712 | 30
|  | 17 | 34.115 | 705 | 32
| 3 | 18 | 34.106 | 702 | 32
|  | 19 | 34.106 | 702 | 32
| 4 | 20 | 34.106 | 702 | 32
| 5 | 21 | 2.106 | 702
|  | 22 | 2.106 | 702
| 6 | 23 | 2.106 | 702
|  | 24 | 31.737
| 7 | 25 | 31.737
| 8 | 26 | 31.737 | 579 | 30
| 9 | 27 | 31.737 | 579 | 30
| 10 | 28 | 31.737 | 579 | 30
3 | 1 | 29 | 32.07
| 2 | 30 | 1.833
| 3 | 31 | 1.833
| 4 | 32 | 1.833
| 5 | 33 | 34.815 | 605 | 33
|  | 34 | 34.815 | 605 | 33
| 6 | 35 | 34.815 | 605 | 33
|  | 36 | 30.728 | 576 | 29
| 7 | 37 | 30.728 | 576 | 29
|  | 38 | 30.728 | 576 | 29
| 8 | 39 | 30.728 | 576 | 29
| 9 | 40 | 36.941
| 10 | 41 | 36.941
4 | 1 | 42 | 33.956 | 652 | 32
| 2 | 43 | 33.956 | 652 | 32
| 3 | 44 | 36.941 | 647 | 35
| 4 | 45 | 36.941 | 647 | 35
|  | 46 | 36.941 | 647 | 35
| 5 | 47 | 36.98 | 660 | 35
|  | 48 | 36.98 | 660 | 35
| 6 | 49 | 33.986 | 662 | 32
| 7 | 50 | 33.226 | 742 | 31
| 8 | 51 | 34.064 | 688 | 32
|  | 52 | 34.064 | 688 | 32
| 9 | 53 | 34.064 | 688 | 32
|  | 54 | 34.064 | 688 | 32
| 10 | 55 | 34.064 | 688 | 32
|  | 56 | 34.064 | 688 | 32
5 | 1 | 57 | 34.109 | 703 | 32
|  | 58 | 34.109 | 703 | 32
| 2 | 59 | 34.109 | 703 | 32
| 3 | 60 | 34.376
|  | 61 | 34.376
| 4 | 62 | 34.376
|  | 63 | 0
| 5 | 64 | 0
|  | 65 | 32.259 | 753 | 30
| 6 | 66 | 32.259 | 753 | 30
| 7 | 67 | 32.259 | 753 | 30
| 8 | 68 | 0
|  | 69 | 30.292
| 9 | 70 | 30.292
| 10 | 71 | 30.728 | 576 | 29
6 | 1 | 72 | 30.728 | 576 | 29
| 2 | 73 | 30.728 | 576 | 29
| 3 | 74 | 34.154 | 718 | 32
| 4 | 75 | 34.154 | 718 | 32
| 5 | 76 | 34.154 | 718 | 32
| 6 | 77 | 43.121 | 707 | 41
|  | 78 | 43.121 | 707 | 41
| 7 | 79 | 34.154 | 718 | 32
|  | 80 | 34.154 | 718 | 32
| 8 | 81 | 32.136
| 9 | 82 | 30.728
| 10 | 83 | 30.728
|  | 84 | 30.728

## Sheet2
G -Irradiance | I -Current
702 | 7.49
605 | 7.17
753 | 8.77
605 | 7.14
576 | 7.04
580
0.19
110.2

## Sheet1
Strings
Inv 1 | 13
Inv 2 | 15
Inv 3 | 13
Inv 4 | 15
Inv 5 | 15
Inv 6 | 13
Total | 84

## Sheet3
Inverter | MPPT | String | No. of modules | Orientation | Tilt angle
1 | 1 | 1 | 16 | 270 | 5
|  | 2 | 16 | 270 | 5
| 2 | 3 | 18 | 270 | 5
| 3 | 4 | 17 | 310 | 5
|  | 5 | 17 | 310 | 5
| 4 | 6 | 17 | 310 | 5
| 5 | 7 | 17 | 310 | 5
| 6 | 8 | 17 | 310 | 5
| 7 | 9 | 19 | 310 | 5
| 8 | 10 | 19 | 310 | 5
| 9 | 11 | 16 | 310 | 5
|  | 12 | 16 | 310 | 5
| 10 | 13 | 16 | 310 | 5
2 | 1 | 14 | 18 | 130 | 5
|  | 15 | 18 | 130 | 5
| 2 | 16 | 18 | 130 | 5
|  | 17 | 18 | 130 | 5
| 3 | 18 | 18 | 130 | 5
|  | 19 | 18 | 130 | 5
| 4 | 20 | 18 | 130 | 5
| 5 | 21 | 17 | 310 | 5
|  | 22 | 17 | 310 | 5
| 6 | 23 | 17 | 310 | 5
|  | 24 | 17 | 310 | 5
| 7 | 25 | 17 | 310 | 5
| 8 | 26 | 17 | 310 | 5
| 9 | 27 | 17 | 310 | 5
| 10 | 28 | 19 | 310 | 5
3 | 1 | 29 | 20 | 130 | 5
| 2 | 30 | 20 | 130 | 5
| 3 | 31 | 20 | 130 | 5
| 4 | 32 | 20 | 130 | 5
| 5 | 33 | 18 | 310 | 5
|  | 34 | 18 | 310 | 5
| 6 | 35 | 18 | 310 | 5
|  | 36 | 18 | 310 | 5
| 7 | 37 | 18 | 310 | 5
|  | 38 | 18 | 310 | 5
| 8 | 39 | 18 | 310 | 5
| 9 | 40 | 18 | 310 | 5
| 10 | 41 | 18 | 310 | 5
4 | 1 | 42 | 17 | 130 | 5
| 2 | 43 | 17 | 130 | 5
| 3 | 44 | 16 | 130 | 5
| 4 | 45 | 16 | 130 | 5
|  | 46 | 16 | 130 | 5
| 5 | 47 | 16 | 130 | 5
|  | 48 | 16 | 130 | 5
| 6 | 49 | 16 | 0 | 5
| 7 | 50 | 17 | 0 | 40
| 8 | 51 | 17 | 0 | 40
|  | 52 | 17 | 0 | 40
| 9 | 53 | 17 | 0 | 40
|  | 54 | 17 | 0 | 40
| 10 | 55 | 17 | 0 | 40
|  | 56 | 17 | 0 | 40
5 | 1 | 57 | 18 | 130 | 5
|  | 58 | 18 | 130 | 5
| 2 | 59 | 18 | 130 | 5
| 3 | 60 | 16 | 40 | 40
|  | 61 | 16 | 40 | 40
| 4 | 62 | 16 | 40 | 40
|  | 63 | 16 | 40 | 40
| 5 | 64 | 17 | 40 | 40
|  | 65 | 17 | 40 | 40
| 6 | 66 | 17 | 40 | 40
| 7 | 67 | 16 | 40 | 40
| 8 | 68 | 18 | 0 | 5
|  | 69 | 18 | 0 | 5
| 9 | 70 | 17 | 0 | 5
| 10 | 71 | 18 | 0 | 5
6 | 1 | 72 | 18 | 130 | 5
| 2 | 73 | 18 | 130 | 5
| 3 | 74 | 19 | 0 | 5
| 4 | 75 | 19 | 0 | 5
| 5 | 76 | 18 | 0 | 5
| 6 | 77 | 19 | 0 | 5
|  | 78 | 19 | 0 | 5
| 7 | 79 | 19 | 0 | 5
|  | 80 | 19 | 0 | 5
| 8 | 81 | 17
| 9 | 82 | 18 | 130 | 5
| 10 | 83 | 18 | 130 | 5
|  | 84 | 18 | 130 | 5
Note on E1: Dayne Sage: Number of modules in Series