## Voc & Isc Test Result
A1 Commissioning - IV Curve Testing | [10 empty] | Site Name
[11 empty] | Tested By: | Date:
I - V CURVE IN STRINGS | [6 empty] | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject |  |  | Your Name Here | The Date
1 | Test carried out during a cloudless interval with irradiance above 600W/m2
2 | Test carried out before connecting the inverters to the loads
3 | Fuses removed prior to connection of the I-V tracer in the case that the PV Facility is connected to the electrical network
4 | Polarity of the strings measured and checked
5 | Measure and record the temperature measured on the backsheet of the PV module (Tm ) for thermographic camera or through the average of the temperature cell sensors
6 | Measure and record the Irradiance on the plane of the PV modules when performing the I-V curve
7 | Measure and record the open circuit voltage Voc across each string through the I-V tracer
8 | Measure and record the short circuit current (Isc ) of the string through the I-V tracer
Notes:
CALCULATIONS
Tc: temperature of the cell of the PV module will be calculated theoretically using the formula:
Tc | Temperature of the cell of the PV module (°C)
Tm | Temperature measured on the backsheet of the PV module (°C)
G | Irradiance on the plane of the PV modules (W/m2)
Gstc | Irradiance in STC (1000W/m2)
∆T | Temperature differences between PV cell and the PV backsheet, considered as 3 °C (as per IEC 61724, table A-1)
INVERTER 1 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 2 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 3 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 4 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 5 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 6 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 7 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 8 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 9 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 10 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 11 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 12 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
INVERTER 13 |  |  | G | Gstc | Tm |  | ∆T | Tc
MPPT 1 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 2 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 3 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 4 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 5 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
MPPT 6 | INPUT 1 |  | 0 | 1000 | 0 |  | 3 | 0
| INPUT 2 |  | 0 | 1000 | 0 |  | 3 | 0
Voc theo : Theoretical open circuit voltage will be calculated theoretically using the formular:
Voc theo | Theoretical open circuit voltage (V)
Nmod | Number of the modules which compose each tested string
Voc stc | Rated PV module open circuit voltage at standard conditions (STC) (V)
δ Voc | PV module manufacturer's rated temperature coefficient of Voc (% / ° C)
Tc | Temperature of the cell of the PV module (°C)
INVERTER 1 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 48.9 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 2 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 3 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 4 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 5 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 6 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 7 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 8 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 9 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 10 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 11 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 12 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 13 |  |  | Nmod | Voc stc | δVoc |  | Tc | Voc theo | Voc meas | 0.95*Voc theo | X *Voc theo
MPPT 1 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 |  | 0 | 46.2 | -0.27% |  | 0 | 0 | 0 | 0 | #DIV/0!
Isc theo : Theoretical short circuit current will be calculated theoretically using the formula:
N | Number of strings which compose each test
Isc stc | Rated PV module short circuit curent at standard conditions indicated in the photovoltaic panel data sheet (STC) (A)
G | Irradiance on the plane of the PV modules (W/m2)
Gstc | Irradiance in STC conditions (1000 W/m2)
δIsc | PV module manufacturer's rated temperature coefficient of Isc (% / °C)
Tc | Temperature of the cell of the PV module (°C)
Isc theo | Theoretical short circuit current (A)
INVERTER 1 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 2 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 3 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 4 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 5 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 6 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 7 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 8 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 9 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 10 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 11 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 12 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
INVERTER 13 |  | N | Isc stc | G | Gstc | δIsc | Tc | Isc theo | Isc meas | 0.95*Isc Theo | X*Isc Theo
MPPT 1 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 2 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 3 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 4 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 5 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
MPPT 6 | INPUT 1 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
| INPUT 2 | 1 | 11.46 | 0 | 1000 | 0.048% | 0 | 0 | 0 | 0 | #DIV/0!
No string may have a measured Voc that differs by less than 5% from the theoretical (Voc > 0.9* Voc theo).
No string may have a measured Isc that differs by less than 5% from the theoretical (Isc > 0.9 * Isc theo).
Strings polarity must be correct.
The accuracy of the I-V tracer and the infrared camera used will be considered.

## Raw Data_Mod Tests
Inverter | MPPT | String | Tc | G | Tm | Voc Measure | Isc Measure | Voc stc Check | N | Gstc | ΔT | Voc theo | Nmod | Voc stc | δ Voc | Tc | Isc stc | δIsc | Isc theo | Tc | Temperature of the cell of the PV module (°C)
1 | 1 | 1 | [7 empty] | 0 | 0 |  | 0 | 48.9 | -0.27% |  | 11.46 | 0.048% |  | Tm | Temperature measured on the backsheet of the PV module (°C)
|  | 2 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | G | Irradiance on the plane of the PV modules (W/m2)
| 2 | 1 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Gstc | Irradiance in STC (1000W/m2)
|  | 2 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | ∆T | Temperature differences between PV cell and the PV backsheet, considered as 3 °C (as per IEC 61724, table A-1)
| 3 | 1 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Voc theo | Theoratical open circuit voltage (V)
|  | 2 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Nmod | Number of the modules which compose each tested string
| 4 | 1 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Voc stc | Rated PV module open circuit voltage at standard conditions (STC) (V)
|  | 2 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | δ Voc | PV module manufacturer's rated temperature coefficient of Voc (% / ° C)
| 5 | 1 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Tc | Temperature of the cell of the PV module (°C)
|  | 2 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | N | Number of strings which compose each test
| 6 | 1 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Isc stc | Rated PV module short circuit curent at standard conditions indicated in the photovoltaic panel data sheet (STC) (A)
|  | 2 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | G | Irradiance on the plane of the PV modules (W/m2)
2 | 1 | 1 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Gstc | Irradiance in STC conditions (1000 W/m2)
|  | 2 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | δIsc | PV module manufacturer's rated temperature coefficient of Isc (% / °C)
| 2 | 1 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Tc | Temperature of the cell of the PV module (°C)
|  | 2 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Isc theo | Theoratical short circuit current (A)
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0 | [6 empty] | Module at
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
3 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
4 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
5 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
6 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
7 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
8 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
9 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
10 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
11 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
12 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
13 | 1 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 2 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 3 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 4 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 5 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
| 6 | 1 | [7 empty] | 0 | 0 |  | 0
|  | 2 | [7 empty] | 0 | 0 |  | 0
Isc theo
Isc theo
Isc theo
Isc theo
Note on J1: Dayne Sage: Number of modules in Series