## Installation Completion
Solar PV Commissioning Report & Procedure
SITE DETAILS
Site Name
Size
Location
Inspector
Installer
| Date |  | 0
PRODUCT DETAILS
| Inverters |  |  |  |  | Qty:
| Modules |  |  |  |  | Qty:
Monitoring
MCCB & Relay
Gen Integration
Checklist of Components Installed
Instructions:
Do not fill in the grey areas as they are not applicable
The first section of the report is a visual inspection of items already completed
The second part requires measements with the necessary measurement tools
Where there are special conditions or items to note please complete the notes area per section
| Please select Yes or No for the following: |  |  |  | Yes/No |  |  | Yes
| You have received the correct module and string layout | [6 empty] | No
You have received the correct SLD
Junction Boxes
Trenching
Walkways & Catladders
DC Units
Sensors/weather station
Generator Integration
Inverter Overhang and/or Enclosure
Visual Installation Inspection Report
TO BE DONE BEFORE COMMISSIONING TESTS
| ROOF |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Has the entry roof report been completed and submitted
| 2 | Is the current roof in good condition
| 3 | Were there existing leaks prior to installation
| 4 | For sheet metals with roof penetrations: Has all holes been sealed
| 5 | High traffic areas: Has there been any damage due to foot traffic
| 6 | High traffic areas: If yes above, has the damaged areas been fixed
| 7 | Has the exit roof report been completed and submitted
Notes:
| PV Sol Design |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Has the modules been installed per the PV Sol design
| 2 | If no, has Emergent been notified of the changes
| 3 | Does the string layout follow the PV Sol design per the Project Description
| 4 | Does the inverter numbering on the PV Sol design follow the inverter numbering onsite
| 5 | Are there obstructions onsite that have not been accounted for in the design?
| 6 | If yes, has Emergent been notified
| 7 | For Solaredge: The layout has been loaded and strung per the as built
| 8 | For Solaredge: The optimizers has been scanned into the correct layout
| 9 | For Solaredge: Optimizer spot check has been done by Emergent
Notes:
| EARTHING |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Has each module been earthed to one another
| 2 | Is there an earthing & bonding arrangement between the arrays
| 3 | Has the cable trays been earthed
| 4 | If there is a Earth busbar, are all connections secure
| 5 | Has the earth cables been terminated with a lug
| 6 | All earthing connections are sound and secure
| MOUNTING STRUCTURE |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Are the module clamps in their clamping zones
| 2 | Are any of the module clamps close to the end of their shortrails
| 3 | All bolts have been torqued and checked
| 4 | For sheet metals: Are any of the module clamps on the locking seams
| 5 | For pitched structures: Has the frames been installed per the drawing, this includes spacing
| 6 | Foundations have been installed correctly
| 7 | Has the structure been grounded
| 8 | Has all unused drilled holes been sealed with an Ejot Screw and silicon
| 9 | If penetrating the roof, holes have been waterproofed
| 10 | No damage to the roof during installation process
Notes:
| PV MODULES |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Modules are aligned in line with one another
| 2 | Corner of modules are not lifting away from sub-structure
| 3 | All modules are in sound and good working condition (no black spots, no deformed/broken cells or frames, etc.
| 4 | Inter-module connectors are properly crimped & securely connected
| 5 | Module clamps are placed within the guideline as set out by supplier
| 6 | PV modules are connected with correct polarity
| 7 | No cables are covering the modules
| 8 | Maintenance strips are adequate for cleaning
Notes:
| MC4 Connections |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | All MC4's have been crimped and tightened with correct tool
| 2 | All MC4's between modules/optimizers have been connected properly
| 3 | Exposed MC4's are covered in adequate trunking
| 4 | No MC4's are lying on the roof
| 5 | All correct connectors have been plugged into one another e.g. MC4 with MC4
| DC CABLES & TRUNKING |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | All cable entries are weather proof and sealed properly
| 2 | Are the cable tray lids secured with long lasting measures
| 3 | Have the string labels been installed on the roof PV
| 4 | All labelling is rated to last in outdoor conditions
| 5 | All cables have been connected per the string layout
| 6 | All cables are selected for current carrying capacity and voltage drop as per approved design
| 7 | Cables are neatly attached to sub-structure/modules
| 8 | Conductors routed are in safe zone or protected against mechanical damage
| 9 | All signage's are appropriate and relevant
| 10 | Trunking is in appropriate position and enclosed/sealed properly. (Check along roof-in building-inverters-main DB)
| 11 | In the event of MC4 connections/extenders, have these been indicated on the trunking and to Emergent Energy
| 12 | Has the cable tray joins and cuts been cold galvanised or protected from environment in some manner
| 13 | Cables are managed neatly in the cable trays and will not pinch in the lid and no sharp edges at cable tray joints/bends
| 14 | If sprague is used between module arrays & module wireways: Is it secured to roof/does not move freely
| 15 | If trunking is used between module arrays & module wireways: Is there adequate protection between the trunking and the module frame
| 16 | Cable trays are properly fixed and does not show excessive deflection
| 17 | Cables within trunking are not at sharp bends, etc.
Notes:
| CHECKLIST FOR DC JUNCTION BOX |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Is the box IP65/67 rated
| 2 | Has it been secured properly
| 3 | Has all strings been labelled
| 4 | Is the box properly sealed to prevent water ingress
| 5 | Are all connections adequate and properly torqued
Notes:
| CHECKLIST FOR TRENCHING |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Are there spares placed in the sleeves
| 2 | Has perforated sleeves been used
| 3 | Is the trench at the correct depth
| 4 | Are the sleeves protected by bedding sand
| 5 | Are the cable sleeves isolated and protected from water pipes
Notes:
| CHECKLIST FOR WALKWAYS & CATLADDERS |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Walkways are properly/securely fixed to the roof sheeting
| 2 | Walkways are installed per the design
| 3 | The spacing between the walkways are adequate and do not show deflection
| 4 | Is the catladder stable and secured to the substructure
| 5 | The catladder is installed per the design
Notes:
| CHECKLIST FOR DC UNIT |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Wiring is as per supplier instruction
| 2 | String fuses are available and inserted
| 3 | Brand: |  | Size:
| 4 | All boxes are properly fixed at appropriate locations & neat
| 5 | DC surge protection devices are available inside the box/inverter
| 6 | Box, related components & insulation rating based on maximum DC voltage
| 7 | Boxes for outdoor use should be suitably rated based on South African climate
| 8 | Gland holes are sealed properly at unused entry points
| 9 | DC isolator is present in DC unit
| 10 | All connections have been checked and torqued, including pre-wired connections
Notes:
| CHECKLIST FOR SENSORS/WEATHER STATION |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Irradiance Sensor/Weather Station/Temperature Sensors: Has the sensor been installed as per the design specification
| 2 | Irradiance Sensor/Weather Station: Is it away from any obstructions/shading
| 3 | Irradiance Sensor: Installed at a slight angle to allow for water runoff
| 4 | Sensors are secured properly
| 5 | Additional sensors are in the correction location
| 6 | The correct sensor/weather station cables have been used
| 7 | Sensor cable are in conduit and protected from external conditions and damage
| 8 | Sensor cables have been labelled
| 9 | Sensor cables do not run alongside any AC cables
| 10 | All test certificates and relevant documentation handed over to Emergent Energy
Notes:
| AC PROTECTION AGAINST OVER-VOLTAGE AND ELECTRIC SHOCK |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Live parts are insulated and protected by barrier/enclosure, placed out of reach
| 2 | Surge protection devices are available
| 3 | External lightning protection system is available or installed, if necessary
| 4 | PV grounding and earthing pass per the previous section
| 5 | All earthing and lightning arrestor checklists have been completed
Notes:
| CHECKLIST FOR INVERTER |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Inverter is installed as per manufacturer’s guideline (mounting and ventilation space)
| 2 | Inverter is properly earthed
| 3 | All ducting and glands are in place and secure
| 4 | Inverter is securely mounted onto the wall
| 5 | Inverter room is well ventilated
| 6 | Inverter for outdoor use shall be suitably rated based on the South African climate.
| 7 | Inverter incoming PV cables are terminated and properly connected as per drawing
| 8 | Inverters have been commissioned as per the suppliers manual
| 9 | String inputs have been labelled
| 10 | Firewalls and fire compartments have been taken into consideration in accordance with the fire protection regulations
| 11 | The inverters are communicating properly with the monitoring platform
| 12 | Inverter serial numbers and inverter inputs have been captured and provided to Emergent Energy
| 13 | Inverters are shaded/protected from direct sunlight and rain
| 14 | Inverters have been labelled
| 15 | RS485 communications cables do not run alongside AC cables
Notes:
| CHECKLIST FOR INVERTER - CONTINUED |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
WIRING - AC
| 1 | Inverter incoming/outgoing cables are adequatly selected for the inverter/circuit breaker rating
| 2 | Inverter incoming/outgoing cables are properly terminated, connected as per drawing and torqued
| 3 | Inverter and inverter breakers are labelled
| 4 | Proper labelling of all the cables and components are done
| 5 | AC cables are properly sized. Please indicate:
| 6 | Inverter grid settings are as per local utility guidelines
| CHECKLIST FOR BATTERY AND COMPONENTS |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Live parts are insulated and protected by barrier/enclosure, placed out of reach
| 2 | Correct designed fuse used for battery cable protection
| 3 | Correctly rated cabling used for battry connections
| 4 | Battery cables are protected by using appropriate wireways/trunking
| 5 | Battery communication cables correctly selected and installed
| 6 | Battery unit adequately placed and secured to avoid shifting or toppling
| 7 | Battery housing has been properly bonded
| CHECKLIST FOR AC DISTRIBUTION BOX |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | AC-DB is properly mounted as per design document
| 2 | Sufficient free space available around and inside the DB to prevent heat generation
| 3 | In the event of heat build up, the DB has an extraction fan
| 4 | All cables have been labelled
| 5 | AC-DB is properly earthed
| 6 | The connections for phase sequence L1, L2 & L3 are in proper order (for three phase inverters)
| 7 | PV DB is shaded from direct sunlight and rain
| 8 | Incoming/outgoing cables are properly connected and terminate as per approved schematic diagram
| 9 | Cables have been heat shrinked properly
| 10 | Proper tagging (NRS097 code) of all cables and components are done
| 11 | All cable glands are properly secured & sealed
| 12 | PV DB conforms with the SLD
| 13 | Inverter and main solar breaker is rated for current carrying capacity
| 14 | Inverter AC cables are properly sized based on current and breaker size
| 15 | AC cables are properly sized. Please indicate:
| 16 | All connections have been checked and torqued
| 17 | Boxes for outdoor use shall be suitably rated based on South African climate
| 18 | Cable bends are not too small in radius and are mechanically protected
| 19 | RS485 communications cables do not run alongside AC cables
| 20 | Shielded RS584 cable was used
Notes:
| CHECKLIST FOR AC BREAKER IN CLIENT DB |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | AC-DB is properly mounted as per design document
| 2 | The relay is powered and drawing reference from the grid side of the clients solar breker
| 3 | The breaker is 4-Pole (or solar breaker is 4-Pole)
| 4 | The UPS is drawing power from the grid side of the clients solar breker
| 5 | Cables have been heat shrinked properly
| 6 | All connections have been checked and torqued
| 7 | AC breaker is rated for current carrying capacity
| 8 | Breaker/meter/relay has been adequately labelled
| 9 | Inverter AC cables are properly sized based on current and breaker size
| 10 | AC cables are properly sized. Please indicate:
| 11 | Take a photo of the trip settings of the grid relay (if applicable)
| 12 | Proper tagging (NRS097 code) of all cables and components are done
| 13 | A grid loss test has been conducted to insure anti-islanding is functional
| 14 | Cable bends are not too small in radius and are mechanically protected
| 15 | Shielded RS584 cable was used
Notes:
| CHECKLIST FOR CABLE IDENTIFICATION AND CABLE ROUTING INSPECTION |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | All power cable routes & locations are as per drawing
| 2 | All cables are properly tagged
| 3 | Cable caution tape is used for all underground cables as per regulation
| 4 | All trunking and conduits are installed as per design document
| 5 | All wiring is in neat condition
| 6 | No damage to cables is permitted
| 7 | All potential hazards are irradiated
| 8 | Trunking is per wiring code
| 9 | The COC has been handed to Emergent Energy
| CHECKLIST FOR MONITORING SYSTEM |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Local & remote communication & data logging system is available
| 2 | Identification marks on communication cable are available and as per regulations
| 3 | Communication system architecture diagram is displayed near the computer in the control room
| 4 | Gap/seperation maintained between power cables and signal cables routing
| 5 | Shielded RS485 or applicable cable was used
| 6 | External communications has been established
| CHECKLIST FOR GENERATOR INTEGRATION |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | The SLD was followed
| 2 | The communication board and controller is connected to a backup UPS
| 3 | The gen meter installed and reading properly, CT's as well
| 4 | The gen meter labelled
| 5 | All generator communication cables are protected and isolated from AC cables
| 6 | The correct communication cable was installed
| 7 | Has generator integration testing been completed during sunlight hours with actual grid loss
| 8 | The SLD is available and stored in a DB onsite
Notes:
| CHECKLIST FOR INVERTER OVERHANG & ENCLOSURE |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | The inverter overhang provides sufficient cover to the inverters
| 2 | The outdoor rating of the overhang can protect the inverters from outdoor weather conditions
| 3 | The inverter overhang is secured properly to a wall/frame
| 4 | The inverter enclosure is secured properly to a wall/frame
| 5 | The inverter enclosure is stable
| 6 | The enclosure has sufficient ventilation
| 7 | Where applicable: The enclosure protects the inverter from outdoor weather conditions
Notes:
| METER |  |  |  |  | Inspection 1 Accept / Reject | Inspection 2 Accept / Reject
| 1 | Has the meter been installed correctly, CT direction checked
| 2 | The correct CT's have been used
| 3 | If converters or rowgowski's have been used, has the converters been powered up
| 4 | Is the meter connected to the inverter/datalogger & in working condition
| 5 | All parameters are properly configured per requirement
| 6 | Have you installed protection at the meter? Note the details below
| 7 | Has the master inverter/logger been programmed for the meter?
| 8 | Is the meter powered up per the SLD, between client solar breaker and grid supply
| 9 | Shielded RS485 or applicable cable was used
| 10 | Is the cabling in a neat and tidy condition
Notes:

## Installation Test Report
Testing Installation Inspection Report
ATTACH SLD AND STRING LAYOUT
1 page per inverter
INVERTER _______________ SERIAL NUMBER _________________
Test point |  | All new cables
Reason for test |  | Testing is performed on to confirm correct voltages, amps and no earth leakage
Use appropriate tools to measure and record (eg. Seaward, Sonel PV tester)
Instructions |  | - When testing DC off, test with DC switch disconnected
- When testing + to Earth and - to earth, DC must be off
- For SolarEdge no need to test voltage for DC on. Confirm DC voltage from the screen/app. When testing the DC ensure that the fuses are open
- For Huawei confirm DC on voltage with Sun2000 App
- For others confirm with what is available
- Test continuity if there are fuses
- To test insulation resistance, the system must be off and disconnected from the inverter and you need a Seward or Megohmmeter. Set meter to 1000V. SURGE PROTECTION MUST BE DISCONNECTED & fuses open
Reject if: |  | - Voltage readings do not line up with the string layout
- SE: High voltage between strings when system is offline i.e. anything greater than 20V
- Insulation resistance is greater than 0.2 ohms
Earthing |  | Circle the method of earthing here:
Earthing results can be completed in the table below or in the earthing tests section
|  | Per String | Per Inverter | Per Arrray | Per Roof
MPPT/ String | Module count | DC Voc (+-) | + to Earth (>1M.ohm) | - to Earth (>1M.ohm) | Module temperature | String Isc (Ampere) | Irradiation (W/m2)
1 String 1
1 String 2
2 String 1
2 String 2
3 String 1
3 String 2
4 String 1
4 String 2
5 String 1
5 String 2
6 String 1
6 String 2
7 String 1
7 String 2
8 String 1
8 String 2
9 String 1
9 String 2
10 String 1
10 String 2
11 String 1
11 String 2
12 String 1
12 String 2
BATTERY |  | Fuse amps | DC Off V (+-) | DC On V (+-) | + to Earth (>1m.ohm) | - to Earth (>1m.ohm) | Earth Result
1
2
3
4
Earthing Tests: Area ______
| Bonding Continuity Tests for: Less than 0.2ohm |  | Mounting Structure
Modules
Trunking
| Comments: |  | If failed or any comments:
| Continuity Tests for: Less than 0.2ohm |  | Each earth cable from PV system
Earthing Tests: Area ______
| Bonding Continuity Tests for: Less than 0.2ohm |  | Mounting Structure
Modules
Trunking
| Comments: |  | If failed or any comments:
| Continuity Tests for: Less than 0.2ohm |  | Each earth cable from PV system
Earthing Tests: Area ______
| Bonding Continuity Tests for: Less than 0.2ohm |  | Mounting Structure
Modules
Trunking
| Comments: |  | If failed or any comments:
| Continuity Tests for: Less than 0.2ohm |  | Each earth cable from PV system
Earthing Tests: Area ______
| Bonding Continuity Tests for: Less than 0.2ohm |  | Mounting Structure
Modules
Trunking
| Comments: |  | If failed or any comments:
| Continuity Tests for: Less than 0.2ohm |  | Each earth cable from PV system
AC TESTS - To comply with SANS 10142-1
| Test point |  | Test at the inverter
| Reason for test |  | Testing is performed on to confirm correct voltages, amps and no earth leakage
Use appropriate tools to measure and record
| Instructions |  | - Switch off PV system
- Breaker must be on for testing
- Closely monitor readings throughout the duration of each test, abnormal fluctuations may indicate damaged insulation
- Disconnect from surge protection for insulation resistance test
| Reject if: |  | - Voltage readings do not line up with the grid standard
| Inverter Breakers & Inverter Voltages | [5 empty] | @ Inverter
L1 to N
L2 to N
L3 to N
L1 to L2
L1 to L3
L2 to L3
N to Gnd (Less than 2V)
CONTINUITY
Continuity of bonding
Resistance of earth continuity conductor
| Solar Main Breaker | [5 empty] | Main Breaker
L1 to N
L2 to N
L3 to N
L1 to L2
L1 to L3
L2 to L3
N to Gnd (Less than 2V)
| Client Main Breaker | [5 empty] | Main Breaker
L1 to N
L2 to N
L3 to N
L1 to L2
L1 to L3
L2 to L3
N to Gnd (Less than 2V)
| Relay |  |  |  |  | Details
Relay Brand
Reference points for relay
Voltage upper and lower parameters
Frequency upper and lower parameters
CONSUMPTION METER - SN ______________
| Test points/ Measure |  | Power Supply
Voltage reference
CT type/ratio
FOR JANITZA/Acurev
| Instructions |  | Ensure the consumption meter is programmed properly
Resistor is instsalled in the proper place (22/23)
The measured values for the above test points should reflect the same values as on the meter
Check the direction of the CT's by confirming the correct values on the meter with the PV system off
FOR SOLAREDGE METERS
| Instructions |  | SWITCH OFF / DISCONNECT the following:
- Red DC switch on inverters
- Connect to master inverter via setapp
- Go to the status and then meter
- Ensure direction per phase is all the same.

## Battery Commissioning
| Tel: | +27 21 828 4202 +27 11 028 8060
| E-mail: | info@emergy.co.za
| Physical: | 19 Queenspark Avenue, Salt River, Cape Town
89 Bute Lane, Sandton, Johannesburg
| Postal: | PO Box 23877, Claremont 7735
Battery Commisioning Certificate
Project: |  | 0 |  |  |  | Commissioning Date: | 0
Date: | [5 empty] | Handover Date:
Battery Details
| Battery 1 |  |  |  |  | Battery 2
| Battery Brand |  |  |  |  | Battery Brand
| Battery Type |  |  |  |  | Battery Type
| Battery Rating |  |  |  |  | Battery Rating
| Battery CB/Fuse rating |  |  |  |  | Battery CB/Fuse rating
| Battery 3 |  |  |  |  | Battery 4
| Battery Brand |  |  |  |  | Battery Brand
| Battery Type |  |  |  |  | Battery Type
| Battery Rating |  |  |  |  | Battery Rating
| Battery CB/Fuse rating |  |  |  |  | Battery CB/Fuse rating
| Battery 5 |  |  |  |  | Battery 6
| Battery Brand |  |  |  |  | Battery Brand
| Battery Type |  |  |  |  | Battery Type
| Battery Rating |  |  |  |  | Battery Rating
| Battery CB/Fuse rating |  |  |  |  | Battery CB/Fuse rating
Battery - Voltage Checks
| Test Results |  | BMS functional (Y/N) | Vdc above fuse | Vdc below fuse | Vdc on DC box/inverter | DC + to earth | DC - to earth | Earth bonding ≤0.2 ohm
Battery 1
Battery 2
Battery 3
Battery 4
Battery 5
Battery 6
Battery Commissioning
| Commissioning Type |  | Firmware updated (Y/N) | Breaker functional (Y/N) | BMS communi-cating (Y/N) | Battery profile/protocol correct (Y/N) | Inverter reading BMS (Y/N) | Battery charge setting (A) | Battery discharge setting (A)
Battery 1
Battery 2
Battery 3
Battery 4
Battery 5
Battery 6
Notes:
Note on C10: Robert: Project Name + peak power

## Meter Commisioning Certificate
| Tel: | +27 21 828 4202 +27 11 028 8060
| E-mail: | info@emergy.co.za
| Physical: | 19 Queenspark Avenue, Salt River, Cape Town
89 Bute Lane, Sandton, Johannesburg
| Postal: | PO Box 23877, Claremont 7735
Meter Commisioning Certificate
Project: |  | 0 |  |  |  | Commissioning Date: | 0
Date: | [5 empty] | Handover Date: | #VALUE!
Meter Details
Meter Brand
Meter Type
|  |  | Production | Consumption | Export/Import
Metered data
Voltage Checks
| Test Results |  | V1 - V2 | V2 - V3 | V3 - V1 | V1 - N | V2 - N | V3 - N | N - PE
At Meter Breaker
On the Meter
Current Transformer Checks
CT Brand
CT Size
CT Direction
CT location
Connection Type and testing
| Connection Type |  | Ethernet | Router | GSM Modem
Select Applicable:
Data Plan
Tested
Notes:
Note on C10: Robert: Project Name + peak power

## Fault Notification Form
Tel: | +27 21 828 4202 +27 11 028 8060
E-mail: | info@emergy.co.za
Physical: | 19 Queenspark Avenue, Salt River, Cape Town
89 Bute Lane, Sandton, Johannesburg
Postal: | PO Box 23877, Claremont 7735
Fault Notification Form
Project: | 0 |  |  |  | Notified By:
Handover Date: | 0 |  |  |  | Date Notified:
CLIENT
Please explain the fault? | [6 empty] | Client to xplain the issue as found
What is your proposed resolution method? | [6 empty] | What the client wants
EMERGENT ENERGY
Investigation | [6 empty] | Response from EE
|  | Yes No | Justification
Fault Classification installation/component | [6 empty] | Refer to the contract definition, any open items, consequential damages from client, lack of maintenance etc etc
Fault Resolution | [6 empty] | What is proposed / agree interanlly to rectify
EMERGENT ENERGY |  | Yes No | Action |  |  | Date Closed
Fault Rectified
Client Acceptance :
Project Manager :
|  |  | Name | Signature | Date
Note on C10: Robert: Project Name + peak power

## O&M Handover
Solar PV Handover to O&M Checklist
SITE DETAILS
| Site Name |  | 0
| Size |  | 0
| Location |  | 0
| Inspector |  | 0
| Installer |  | 0
| Date |  | 0
PRODUCT DETAILS
| Inverters |  | 0
| Modules |  | 0
| Monitoring |  | 0
Projects to Matriarch Questionnaire
| Documentation |  |  |  |  | Yes / No
| 1 | Documents saved per the Documents Requirements sheet?
| 2 | Final Yield confirmation from design engineer or business developer
| 3 | Roof type _______________________
| 4 | SolarEdge: Site mapper completed, loaded and correct?
| 5 | Is there gen integration? If yes, who installed it?
| 6 | Gen details provided? Which gen integration device was used _________________
| 7 | Is there any other generator installed onsite?
| 8 | Does export limitation need to be activated?
| 9 | Is the clients phases balanced?
| 10 | Purchase Contract Type: Out right purchase LTO Roof Rental
| 11 | Maintenance Contract Type: Monitoring O&M PG
| 12 | Are there any other monitoring platform details? Save in Document Requirements sheet
| 13 | Internet provider? __________________
| 14 | Has physical shutdown of the system been done in order to test the generator integration
| 15 | Has a grid isolation test on the clients solar breaker been conducted? "Loadshedding"
| 16 | Is the communication system connected to a backup supply?
| 17 | Are there waterpoints onsite
| 18 | Are there major shading obstructions?
Notes:
| Onsite Contact/Access Details |  |  |  |  | Yes / No
| 1 | Who installed the PV system? ______________________________ Provide contact details below.
| 2 | Owner name, contact number and contact email: ________________________________________________ Portfolio Client?_______________________
| 3 | Maintenance contact name, contact number and contact email:
| 4 | Is there security control when accessing the site? Provide access details below Yes No
| 5 | Detail H&S requirements. I.e. Do we need to submit a H&S file, wear harness, etc.?
| 6 | List inverter access details. I.e. Padlock key to be collected at security, ladder, location, etc.
| 7 | List combiner box access details. I.e. Padlock key to be collected at security, ladder, location, etc.
| 8 | List roof access details. I.e. Padlock key to be collected at security, ladder, etc.
| 9 | Is the clients Main DB and our Solar DB in separate locations? Provide location details
| 10 | Additional site or client points to be raised:
Notes:
|  | Project Manager: |  | Sign: | Date:
|  | Asset Manager: |  | Sign: | Date:
Note on C52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Data source by priority 1. Signed yield in CP 2. Data Tool 3. PV Sol 4. Costing Sheet

## Document Requirements
Phase | Document | Responsible | Location
Pre-Construction | Final Costing Sheet | Sales | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\0. Planning\Final Costing and CP
| Signed Cost Proposal | Sales | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\0. Planning\Final Design Details
| Signed O&M Contract | Sales | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\1. Contractual and Admin
| Consumption Details/Considerations | Sales/Designer | To be discussed with Sales/Designer
| Final PV Sol Design | Designer/PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\0. Planning\Final Design Details
| CSV File from PV Sol | Designer/PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\0. Planning\Final Design Details
| Structural Engineers Report | Projects Team | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| Single Line Diagram | Designer/PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\3. Construction\Drawings\Electrical
| If applicable: Spares List | Sales | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| Entry Roof Report | Projects Team | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| SSEG Documentation Installation Approval | Designer | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\SSEG
Post Construction | Red Team Inspection Forms | Red Team | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\5. Quality Control
| Inverter Seward Test Results/Commissioning Forms | PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Forms
| Continuity Tests | PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Forms
| AC Tests | PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Forms
| Meter Commissioning | PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Forms
| Site Layout Drawing | PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| Communication SLD - with IP's | Designer/PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\3. Construction\Drawings
| Commissioning Report | PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report
| PR Eng Signoff | Projects Team | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\SSEG
| COC | Projects Team | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| Product Datasheets | PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| Product Warranty Documentation | PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| Installer Defects Form | Projects Team | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| EE Defects Form | Projects Team | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| SSEG Documentation Commissioning Approval | Designer | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\SSEG
| Exit Roof Report |  | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\4. Commissioning\Commissioning Report\Appendices
| Photos: | PM | D:\Dropbox (Emergent Energy)\Emergent Energy Team Folder\01 - Clients\01 - active projects (1)\PROJECT_NAME\PM\3. Construction\Photographs
- Inverter Inputs
- Inverter Room
- PV Module Installation
- AC DB: with connections
- Comms DB
- Client Solar Breaker
- Relays: Both
- Client DB Room
- Earthing

## End of Defects
Tel: | +27 21 828 4202 +27 11 028 8060
E-mail: | info@emergy.co.za
Physical: | 19 Queenspark Avenue, Salt River, Cape Town
89 Bute Lane, Sandton, Johannesburg
Postal: | PO Box 23877, Claremont 7735
End of Defects
These Guidelines and Instructions can be include in the RFQ data pack template to be sent to the installer for quoting. The project specification should be expanded to include all of this information as a single source of info for the installer. Also, ICS is to form the basis of the new Installer Completion Certificate and Pre-commission tests
Project: | #VALUE! |  |  |  | Installer: | #VALUE!
Date: |  |  |  |  | For Installer:
For Emergent Energy:
VOLTAGES TO BE COMPARED WITH COMMISSIONING REPORT RESULTS
MOUNTING STRUCTURE | [5 empty] | Pass | Fail
1 | Rust on bolts
2 | Rust on mounting structure
3 | Damaged mounting structure
4 | Module clamps in correct position
Notes:
PV MODULES | [5 empty] | Pass | Fail
1 | PV modules secure in place
2 | No damaged modules
3 | No damaged cells
Notes:
TRUNKING, CABLE ROUTE & COMBINER BOXES | [5 empty] | Pass | Fail
1 | All trunking still in place i.e. in place securely
2 | No cables are exposed in trunking | [7 empty] | OK□ No OK□
3 | All glands still in place | [7 empty] | □ □
4 | Cables are neatly attached to sub-structure
5 | All tagging is still in place | [7 empty] | Emergent Accept / Reject
6 | All tagging is still visible | [7 empty] | Emergent
7 | Combiner boxes securely mounted
8 | Tagging still visible on combiner boxes
9 | Fuses functioning properly
Notes:
CHECKLIST FOR INVERTER | [5 empty] | Pass | Fail
1 | Confirm DC voltage of each MPPT
2 | Confirm DC amps for each MPPT
3 | Confirm AC voltage and amps
4 | Inverter fan replacement warning light not on
5 | All ducting and glands are in place and secure
6 | Inverter labelled
7 | Inverter incoming/outgoing cables are properly connected
8 | All cables are securely in place
9 | All fuses functioning properly
Notes:
CHECKLIST FOR WEATHER STATION & MONITORING SYSTEM | [5 empty] | Pass | Fail
1 | Local & remote communication & data logging system is running
2 | Janitza reading consumption correctly
3 | Solar-log performance is as per the target
4 | Solar-log display in proper working condition
5 | Internet connection is in proper working condition
Notes:
For Installer
For Emergent Energy
|  | Name |  | Signature |  | Inspection Date
VOLTAGE CAPTURE
| INVERTER | MPPT | STRING | # PANELS
| 1 | 1 | 1 | 20
|  |  | 2 | 20
|  | 2 | 1 | 20
|  |  | 2 | 20
| 2 | 1 | 1 | 17
|  |  | 2 | 17
|  |  | 3 | 17
|  | 2 | 1 | 18
|  |  | 2 | 18
Note on C10: Robert: Project Name + peak power