# SOP — Commissioning (CT-led)

Context: Uses your Commissioning Report_Template.xlsm and Simulation Test template.docx. Operating model: CT drives through PM; OE reviews technical data; HoPE does final QA sign-off. Priority: PmP/HoPE. Workload assigning: HoPE. Escalation: CT → OE/PM → HoPE/PmP → COO.

# 1) Purpose

Prove safe, compliant operation of the installed system in all applicable modes.

Demonstrate the system to the Client using the Simulation Test template and obtain Client sign-off.

Create and manage a site-specific Commissioning Snag List (non-negotiable) and close defects before handover.

Capture complete evidence in Commissioning Report (.xlsm) and Simulation Test records; obtain HoPE final QA sign-off.

# 2) Scope & Trigger

In scope:

On-site commissioning for configurations: Grid PV; PV+Gen; PV+BESS (arbitrage/backup); PV+BESS+Gen (arbitrage/backup).

Out of scope:

Construction QA execution; design changes; client training beyond Simulation Test overview; O&M handover.

Trigger:

Project reaches Commissioning; HoPE assigns CT (and supporting OE) and confirms client witness requirements with PM.

# 3) Roles & RACI

| Role | Responsibilities |
| --- | --- |
| CT (Responsible) | Plan, execute tests, run client demonstration, complete xlsm & Simulation Test, compile Snag List, drive retests & evidence. |
| HoPE (Accountable) | Final QA sign-off; ensures client-signed Simulation Test is filed; ensures Snag List status meets policy before sign-off. |
| PM (Consulted / Client Interface) | Book windows; arrange client witness/signatures; manage comms/access; agree snag closure dates with client. |
| OE (Consulted / Reviewer) | Review technical results; approve re-test instructions; mark 'Technically Reviewed' in xlsm. |
| Client Representative (Signatory) | Witness Simulation Test demo; sign Simulation Test acknowledging behaviour per each mode. |
| PmP (Prioritisation) | Set priority; assist with resource conflicts. |

Prioritisation: PmP/HoPE • Workload assigning: HoPE • Escalation: CT → OE/PM → HoPE/PmP → COO

# 4) Artefacts / Tools

Commissioning Report_Template.xlsm (measurement data, evidence links).

Simulation Test template.docx (client-facing demo & sign-off).

PV Tester, multimeter, clamp meters, comms laptop/app access.

Photo/video/log evidence (inverter portal, BMS, generator controller, meters).

# 5) DoR — Definition of Ready

Client witness & sign-off set: PM confirms named Client Rep, time, and place; Simulation Test doc pre-filled with site details.

Snag List ready: blank Commissioning Snag List sheet/log created (in xlsm or linked sheet).

Documents: latest IFC, SLDs, Construction QA output; Commissioning Report (xlsm) created with project metadata.

Instruments & safety: calibrated instruments; PTW/LOTO where needed; comms to inverter/BMS/generator confirmed.

People: CT lead assigned; OE on-call; HoPE available for sign-off window.

If any missing → DoR-Fail (log + notify PM & OE; escalate per path).

# 6) DoD — Definition of Done

Commissioning Report (xlsm) complete with linked evidence.

Simulation Test completed AND signed by the Client Representative (per configuration tested).

Snag List compiled (non-negotiable) and status meets policy: Critical snags = 0 open; Non-critical snags have owners/dates/evidence plan agreed by PM + Client; re-test scheduled if required.

OE 'Technically Reviewed' recorded in xlsm.

HoPE QA sign-off complete.

All files saved to SharePoint [TBC path]; PM notified.

# 7) Procedure — CT leads

7.1 Plan & setup

CT + PM: confirm commissioning window, client witness name, and signing process.

CT: open xlsm; enter project metadata; create Snag List tab/log if not included.

CT: pre-select Simulation Test sections for actual configuration(s).

CT + OE: align acceptance criteria tied to design/utility (anti-islanding times, export limit, BESS thresholds, gen sync ranges).

CT: verify instrument calibration; take photos of meters/testers S/N & cal stickers.

7.2 Execute technical tests — record in xlsm

Perform tests for applicable configurations (Grid PV; PV+Gen; PV+BESS variants; PV+BESS+Gen).

Capture measured values and attach evidence links (photos/videos/logs).

Add snags immediately when deviations found: create entries with description, severity (Critical/Non-critical), owner, due date, evidence required.

7.3 Client demonstration & Simulation Test sign-off

CT (with PM present): walk the Client through the Simulation Test steps live for each applicable mode.

Record observations in the Simulation Test document.

Client Representative signs the Simulation Test per mode tested (name, designation, date, signature).

File signed Simulation Test into SharePoint; paste link into xlsm.

7.4 Snag management (non-negotiable)

Maintain the Snag List throughout commissioning (see table template below).

Critical snags: must be closed and re-tested before DoD.

Non-critical: agree owner/due date with PM + Client; capture in log; schedule re-test/verification; share weekly until closed.

7.5 Technical review & closure

OE: review xlsm + Simulation Test; provide re-test instructions if needed; set 'Technically Reviewed' when acceptable.

CT: complete any re-tests; update evidence and Snag List.

HoPE: verify Client-signed Simulation Test is filed and Critical snags = 0; then sign QA.

CT: file all final docs; notify PM; handover can proceed.

# 8) Acceptance rules (tie back to design/utility)

Anti-islanding & restart within approved limits.

Export limiting respects set point (CT orientation and scaler correct).

Generator integration stable V/F; clean sync; no nuisance trips under load step.

BESS arbitrage follows schedule; BESS backup carries load and respects SoC thresholds; clean transitions.

Monitoring/meters: correct rotation/polarity; timestamps; alarms functional.

Client demo: Simulation Test signed confirming understanding of behaviour.

# 9) Filing & naming (SharePoint)

Path: [TBC Root]/Projects/Client_Site/Commissioning/

01_Commissioning_Report (xlsm)

02_Simulation_Tests (client-signed)

03_Photos_Videos (by TestID)

04_Logs (inverter/BMS/gen/meter)

05_Snag_List (live log + closure proofs)

06_Signed_Approvals (HoPE QA)

Naming: Client_Site_COM_{YYYYMMDD}_{Config}_{Step}.ext

# 10) Quality gates

DoR met (client witness arranged; Snag List ready; docs & tools ready).

Simulation Test signed by Client and filed.

Snag List exists and is current; Critical=0 before sign-off.

OE 'Technically Reviewed' done.

HoPE QA sign-off complete.

# 11) Standard comms (paste-ready)

Client witness invite (PM): Commissioning demonstration for {Site} on {date/time}. We will run the Simulation Test to show system behaviour in applicable modes. Please nominate a representative to witness and sign the Simulation Test.

DoR-Fail (CT → PM/OE): Commissioning cannot start — missing {items}. Please resolve; I’ll proceed once complete.

Snag List issue (CT → Owners, cc PM): New Critical/Non-critical snag {ID}: {desc}. Owner {name}, due {date}. Evidence required: {proof}. Re-test scheduled {date/time}.

Submission for sign-off (CT → HoPE, cc PM/OE): Commissioning complete for {Site}. Attached/linked: Commissioning Report (xlsm), Client-signed Simulation Test, Snag List (Critical=0, Non-critical plan agreed), evidence links. Request QA sign-off.

# 12) KPIs

Client sign-off lead time: end of tests → client signature captured.

Snags at first run: # total / # critical.

Snag closure time: average days to close; % closed on/before due dates.

First-pass acceptance: % tests passing without re-test.

Commissioning duration: start → HoPE sign-off.

# Appendix A — Simulation Test Client Sign-off Block (insert per configuration)

| Configuration Tested | {Grid PV / PV+Gen / PV+BESS (arbitrage/backup) / PV+BESS+Gen} |
| --- | --- |
| Client Representative | Name & Designation |
| Date | YYYY-MM-DD |
| Outcome | Pass / Conditional Pass / Fail (notes) |
| Signature | __________________________ |

# Appendix B — Commissioning Snag List (non-negotiable)

| ID | Area | Description | Severity (Critical/Non-critical) | Owner | Due date | Evidence required | Status (Open/Closed) | Closure proof link |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |