# SOP — Construction QA

Source: Your lifecycle screenshot + provided QA Gate templates. Assignment note: OE or PM assigns a capable person to perform QA inspections. RACI from sheet: Prioritisation — PmP/HoPE; Workload assigning — HoPE; QA sign-off — HoPE; Escalation — OE → PM → HoPE/PmP → COO.

# 1) Purpose

Execute and document construction quality assurance against design intent using the QA Template Forms.

Provide evidence for compliance (SANS/NRS/IEC) and readiness to proceed to next phase or commissioning.

Ensure HoPE performs final QA sign-off with clear escalation.

# 2) Roles & Assignment

| Role | Owner / Notes |
| --- | --- |
| Responsible (inspection execution) | Assigned capable person (by OE or PM) using the QA templates. |
| Accountable (final QA sign-off) | HoPE (Head of Project Engineering) |
| Consulted | PM, PmP (project management) |
| Prioritisation | PmP / HoPE (per sheet) |
| Workload assigning | HoPE (per sheet) |
| Escalation path | OE → PM → HoPE/PmP → COO (per sheet) |

# 3) Trigger & Scope

Trigger:

Construction reaches QA checkpoints as defined in the lifecycle (Gate 1, 2, 3).

Scope:

Use the provided QA Gate templates with no alterations to scope or checks.

Capture Pass/Fail/NA, notes, actions, and photo references exactly in the forms.

Submit completed forms for HoPE review and sign-off.

# 4) Procedure (Step-by-step)

Prioritise & assign: PmP/HoPE confirm priority; HoPE (or PM/OE) assigns a capable inspector.

Prepare: download the correct QA Gate template (1/2/3) and latest design references.

Inspect & record: complete all checks in the template; attach evidence; raise punch items.

Review & rectify: ensure punch items have owners & due dates; recheck closures.

Submit for sign-off: send completed template to HoPE for approval.

Approval & archive: HoPE signs; file to SharePoint; update project status per PM instruction.

Escalate blockers via OE → PM → HoPE/PmP → COO.

# 5) QA Gate 1 — After Mounting Structure Complete (before modules/DC)

Header (fill in): Project | Site | Inspector | Date | Weather | Design Rev | PTW/Method Statement IDs | Photo Set Ref

A. Documentation & Layout

Latest design/layout on site — matches approved drawing (row count, tilt/orientation, setbacks, walkways).

Structural sign-off (roof/ground) — engineer’s approval on record.

Hold points briefed — crew understands QA gates & torque spec sheets.

B. Mechanical Fixings & Integrity

Roof anchors/rails per pattern & substrate; spacing per design.

Torque of structural fasteners — recorded vs manufacturer spec (sample ≥10% or min 10 per block).

Waterproofing/penetrations — sealed; no capillary paths; water test if required.

Corrosion protection — compatible metals; coatings intact.

Clearances & walkways — safe access; walkway tiles/rails installed where required.

Edge distances & wind zones — setbacks/bracing per design.

C. Earthing/Bonding & LPS Interface

Structural bonding (rails/anchors) — mechanical bonds installed; continuity path planned to main earth.

Equipotential conductors — sized & routed per design; protected.

LPS coordination (if present) — separation distances/air-terminations per lightning study.

D. Cable Support (pre-wire)

Trays/conduits/brackets fitted — UV-rated, secure; drain holes where needed.

No shared trunking AC/DC — segregation planned and physically separated.

E. Labelling/Signage (pre-placement)

Preliminary PV hazard labels — planned at roof access, combiner/isolator locations.

STOP/GO: Proceed to Gate 2 only when structural QA is pass and punch items are closed.

# 6) QA Gate 2 — After DC Cabling & Module Installation (before energising)

Header (fill in): Project | Site | Inspector | Date | Design Rev | String Map Rev | Test Equipment (model/SN/cal)

A. Modules & Mechanical

Orientation/tilt & clamping zones — match design; clamps within manufacturer window.

Module serial capture — 100% serials recorded; as-built module map complete.

Clamp torque — logged vs spec; sample ≥10% per block.

B. DC Cabling, Connectors, Routing

Cable type/size — PV cable to IEC 62930/EN; sized for current/volt-drop & temperature.

Connectors — same type/brand; crimped with approved tool; IEC 62852 compliant.

Routing & support — no sharp radii/chafe/ponding; UV/heat protected; secured every 300–500 mm (site dependent).

DC segregation — DC separate from AC; no shared enclosures unless segregated.

C. Protection & Isolation (DC)

String/combiner fusing — required where reverse current possible; PV fuses ≥1.56×Isc if applicable.

DC isolators — load-break isolators at array/combiner and at inverter; DC-rated.

Surge protection (DC) — SPD Type II at array/combiner/inverter as designed; short/straight earthing conductors.

Labels — polarity, string IDs, voltage hazard warnings at boxes and isolators.

D. Electrical Tests — record values & tolerances (IEC 62446-1)

| Test | Acceptance criteria | Ref | Result / Limit | Pass/Fail |
| --- | --- | --- | --- | --- |
| Continuity of protective bonding | < 1 Ω continuous path from frames/rails to earth | IEC 62446-1 |  |  |
| Polarity check (all strings) | Correct polarity at combiner/inverter; no cross-mating | IEC 62446-1 |  |  |
| Open-circuit voltage (Voc) per string | Within design tolerance across strings (~±5% after temp correction) | IEC 62446-1 |  |  |
| Short-circuit current (Isc) per string | Within design tolerance; similar orientation strings ±5–10% | IEC 62446-1 |  |  |
| Insulation resistance | ≥ 1 MΩ at correct test voltage (per OEM limits) | IEC 62446-1 |  |  |

STOP/GO: Only progress to AC/tie-in & inverter works when all DC tests pass, punch items are closed, and string map + test sheets are filed.

# 7) QA Gate 3 — AC Tie-in, Inverters, Utility Interface (pre-commissioning)

Header (fill in): Project | Site | Inspector | Date | Utility | SSEG Ref | Inverter Model/Qty | Firmware | Export-limit? (Y/N)

A. Inverter Installation & Environment

Mounting & clearances — per OEM; ventilation clear; IP rating suits location.

Inverter approval — model listed on municipal/NRS type-tested list; certificate on file.

DC & AC gland entries — correct glands; drip loops; strain relief.

Labelling — inverter ID; AC/DC isolators; hazard labels; single-line near equipment.

B. AC Distribution, Protection & Earthing

AC cable sizing & terminations — sized for current/volt-drop; lugs crimped; torque logged.

Main AC isolator — lockable, visible break; labelled.

Overcurrent/MCB settings — ratings per design; fault-level check done.

AC Surge protection — SPD Type II at inverter AC output/main DB as designed.

Neutral-earth arrangements — correct earthing system; no illegal N–E bonds downstream of RCD.

RCDs/ELDs (if applicable) — correct type/rating; trip test recorded.

C. Utility Interface & Grid Compliance

Anti-islanding & protection settings — per NRS 097-2-1 (U/F, ROCOF if applicable, reconnection delays).

Export limiting / zero-export — CTs/meters oriented; limiter commissioned; setpoint per utility approval.

Utility approval docs — SSEG application; type-test summary; SLD; protection schedule on file.

D. Metering, Monitoring, Communications

Revenue/plant meters — CT polarity & burden; phase rotation; time sync.

SCADA/portal connectivity — inverters online; data valid; timezone set; alarms tested.

Alarms & notifications — grid loss, inverter trip, DC insulation alarms verified.

E. Pre-Commissioning Electrical Tests (record)

| Test | Acceptance criteria | Ref | Result / Limit |
| --- | --- | --- | --- |
| Earth continuity | Protective earth continuity verified through all enclosures | IEC 62446-1 |  |
| Functional protection trip tests (witness if required) | Demonstrate trip at set U/F thresholds and reconnection delay | NRS 097-2-1 / Municipal |  |
| Phase rotation & voltages | Correct rotation; voltages within utility limits | NRS 097-2-1 |  |

STOP/GO: Only energise and start formal commissioning once protection settings, export control and AC safety checks are signed off.

# 8) Filing & Admin Artifacts (per gate)

Type-test evidence for inverters (NRS 097-2-1).

SANS 10142-1/-1-2 compliance for wiring, labelling, isolation, SPDs, DC protection; CoC issued by a qualified person.

PV GreenCard-style pack (photos, serials, test results, user manuals).

Connector compliance: mated pairs to IEC 62852 only; no cross-mating.

# 9) Sign-off

Inspector (capable person): ____________________   Date: ____________

HoPE (final QA sign-off): _______________________   Date: ____________